JEFFERSON SPRINKLER, INC.
	❑ 
	FLOW TEST SUMMARY
	❑



	Project:     
	

	Address:   2100 St Thomas St., New Orleans   
	 Standard Instrument Co.

	Date:         10-9-15 
Time:        8:20 am 
	                                        Conducted By: Karl Hinkel

                                                                 Eric Daigle       

	

	Test Hydrant: # 1

	Location:    St. Thomas St. @ Jackson Ave.                                                       

	Static Pressure (no water flowing):    40 psi
	Residual Pressure (while water flowing):     37  psi

	

	Flow Hydrant: # 2
	
[image: image1.wmf]
This butt used

	Location: St. Thomas St. near Josephine St.

	Flow:        555 gpm
	

	

*Sketch hydrant locations with respect to building/hazard*


   
[image: image2]
JEFFERSON SPRINKLER, INC.  p.o. bOX 129, GRETNA, LA.  70054  (504) 393-7699, fax: (504) 367-0215

CROMWELL ARCHITECTS ENGINEERS, INC.  101 SOUTH SPRING ST., LITTLE ROCK, AR.  72201  (501) 372-2900, fax: (501) 372-0482


_1095678636.wmf

