

SECTION 16120PRIVATE 

WIRE AND CABLE
PART 1 - GENERAL


1.01

RELATED SECTIONS
A. Drawings
B. Division 01 – Specification Section

C. Section 16010 – Basic Electrical Requirements.

1.02
SUMMARY
A. The work of this section consists of providing labor, materials, tools, appliances and miscellaneous accessories associated with the electrical wire and cable work indicated by the Drawings and Schedules.
B. Types of wire, cable and connectors in this section include the following:

1. Copper conductors

2. Copper-sheathed cable

3. Fixture wire

4. Ground wire

5. Service-entrance cable

C. Applications for wire, cable and connectors required for project are as follows:

1. Power distribution circuitry

2. Lighting circuitry

3. Appliance and equipment circuitry

4. Motor-branch circuitry

PART 2 – PRODUCTS


2.01

MANUFACTURERS

A. Available Manufacturers:  Subject to compliance with requirements, provide products of one of the following (for each type of wire and cable):
1. Wire and Cable

a. Alcan Cable

b. American Insulated Wire and Cable

c. Belden

d. Cerro Wire and Cable Co.

e. Okonite Co.

f. Phelps Dodge Wire & Cable

g. Southwire

2. Connectors:

a. AMP, Inc.

b. Appleton Electric Co; Emerson Electric Co.

c. Burndy Corporation

d. Brand-Rex Div, Pyle National Co.

e. Electrical Prodcuts, Div; Midland-Ross Corp.

f. General Electric Co.

g. ITE

h. Ideal Industries, inc.

i. Leviton Mfg Company

j. 3M Company

k. O-Z/Gedney Co.

l. Southport Industries Inc.

m. Square D Company

n. Thomas and Betts Corp.
2.02

WIRE AND CABLE
A. General
1. Except as otherwise indicated, provide UL listed wire, cable and connectors of manufacturer’s standard materials, as indicated by published product information, designed and constructed as recommended by manufacturer, and as required for the installation.

B. 600 Volt Building Cable and Wire:
1. Provide soft of annealed copper wires meeting, before stranding, the requirements of ASTM B3, “Standard Specification for Soft of Annealed Copper Wire for electrical Purposes,” latest edition.

C. Branch feeder and circuit conductors shall be copper, single conductor heat and moisture resistant and thermal plastic insulated for all sizes, rated 600 volts, stranded.  Use solid wire up to #10 for final connection to wiring devices with screw terminals.
D. Lighting branch circuit wiring and motor control wiring shall be suitable for 60°C operating temperature, of types appropriate for dry or wet locations.


Feeders, sub-feeders, and motor power wiring regardless of size shall be rated 600 volts and shall be suitable for 75°C operating temperature, of types appropriate for dry and wet locations.

E. Fixture wiring shall be 14 or 16 gauge, stranded, rated 600 volts and shall be suitable for 90°C operating temperature, (150°C under high temperature operating conditions) of types appropriate for dry or wet locations.

F. Unless otherwise specified, wire for the various services shall be of the following types:

1. Branch lighting circuits, Type “THW” or “THNN/THWN,” or type NMC cable.

2. Branch power circuit, Type “THW” or “THWN”, or type NMC cable.

3. Main feeders and sub-feeders, Type “THW” or “THHN/THWN” copper.

4. Fixture wiring, Type “TFFN” (Type “SFF” or high temperatures).

5. Motor control wiring, Type “TW.”

G. Insulation:  Insulation shall meet or exceed the requirements of UL 83, “Standard for Thermoplastic Insulated Wires.”

1. Insulation for conductors sized No. 18 AWG through No. 10 AWG shall be UL Type THW, THHN/THWN.

2. Insulation for conductors sized No. 8 AWG and larger shall be UL Type THW, THHN/THWN.
3. All wiring inside lighting fixtures shall be temperature rated per the NEC.

4. Branch circuit wiring within 3” of fluorescent ballasts shall be temperature rated for 90°C.

PART 3 – EXECUTION


3.01

INSTALLATION
A. General:  Install electrical cable and wire as indicated, in compliance with manufacturer’s written instructions, applicable requirements of NEC and NECA’s “Standard of Installation,” and in accordance with recognized industry practices.
B. Coordinate cable and wire installation work with electrical raceway and equipment installation work, as necessary for proper interface.

C. Pull conductors together where more than one is being installed in a raceway.

D. Use pulling compound or lubricant, where necessary; compound must not deteriorate conductor or insulation.  Use only U.L. listed lubricant.

E. Use pulling means, including fish tape, cable or rope which cannot damage raceway.

F. No conductor shall bear more than eighty percent (80%) of its rated ampacity.  All conductors, including neutrals, shall be tested under full load conditions to ensure proper loading.

G. Wiring, Emergency System:  Wiring from emergency source of emergency source distribution overcurrent protection to emergency loads shall be kept entirely independent of other wiring and equipment and shall not enter the same raceway, cable, box or cables with other wiring.

H. Keep conductor splices to minimum.  Feeder conductor splices are not allowed unless approved by Architect.

I. Use splice and tap connectors which are compatible with conductor material.

J. The system shall be properly grounded and continuously polarized throughout following the color coding specified.

K. In general, conductors shall be of the same size from the last protective device to the load.

L. Do not pull conductors into raceways until raceway system (including all outlets, cabinets, bushings and fittings) is completed.  Verify that all work of other trades which may cause conductor damage is completed.  Use only approved cable lubricants when necessary.

M. On termination at branch circuit outlets leave a minimum of eight inches (8”) free conductor for installation of devices and fixtures.

N. Cover uninsulated splices, joints and free ends of conductor with rubber and friction tape fo PVC electrical tape.  Plastic insulating caps may serve as insulation.

O. Do not use mechanical means to pull wire No. 8 or smaller.

P. Branch circuit conductors shall not be smaller than #12 AWG and shall be sized as required by the load served and for specific NEC requirements.  Conductors for 20 amp branch circuits of 120 volts, more than 100 ft. long (to the first fixture or other current-consuming outlet) shall be No. 10 AWG.

Q. Branch circuit wires which come within 3” of a ballast within a light fixtures, e.g., wires running through end-to-end connected fluorescent fixtures, must be rated for 90°C.

R. Control circuit conductors shall be #14 AWG, stranded.  Contractor responsible for sizing conductors for voltage drop.

S. All single conductor cables shall be installed in conduit.

T. Ground conductors #6 AWG and smaller shall either be bare metal or have green insulation.  Ground conductors larger than #6 AWG shall have a minimum of 6” taped with green tape at all terminations and/or splices.

U. Use anti-short insulating bushings to protect wires at the ends of the armor on Type Ac cable.


3.02

FIELD QUALITY CONTROL
A. Prior to energization, test cable and wire for continuity of circuitry, and also for short circuits.  Correct malfunctions when detected.
B. Subsequent to wire and cable hook-ups, energize circuitry and demonstrate functioning in accordance with requirements.

END OF SECTION

08112.13 / Crosswinds Apartments 
16120 - 1 
WIRE AND CABLE

