
SECTION 15936PRIVATE 


AIR OUTLETS AND INLETS

1 PART 1   GENERAL


1.01

WORK INCLUDED



A.
Diffusers.



B.
Diffuser boots.



C.
Registers/grilles.



D.
Door grilles.



E.
Louvers.


1.02

seq level2 \h \r0 

RELATED WORK




Not Used


1.03

seq level2 \h \r0 

REFERENCES



A.
ADC 1062 ‑ Certification, Rating and Test Manual.



B.
AMCA 500 ‑ Test Method for Louvers, Dampers and Shutters.



C.
ANSI/NFPA 90A ‑ Installation of Air Conditioning and Ventilating Systems.



D.
ARI 650 ‑ Air Outlets and Inlets.



E.
ASHRAE 70 ‑ Method of Testing for Rating the Air Flow Performance of Outlets and Inlets.



F.
SMACNA ‑ Low Pressure Duct Construction Standard.


1.04

seq level2 \h \r0 

QUALITY ASSURANCE



A.
Test and rate performance of air outlets and inlets in accordance with ADC Equipment Test Code 1062 and ASHRAE 70.



B.
Test and rate performance of louvers in accordance with 




AMCA 500.


1.05

seq level2 \h \r0 

REGULATORY REQUIREMENTS



A.
Conform to ANSI/NFPA 90A.


1.06seq level2 \h \r0 

WALL SUPPLY REGISTERS/GRILLS



A.
Streamlined and individually adjustable blades, depth of which exceeds 3/4 inch (19 mm) maximum spacing with spring or other device to set blades, face, double deflection. 



B.
Fabricate 1‑1/4 inch margin frame with concealed mounting and gasket.



C.
Fabricate of steel with 20 gage (0.90 mm) minimum frames and 22 gage (0.80 mm) minimum blades, steel and aluminum with 20 gage (0.90 mm) minimum frame, or aluminum extrusions, with factory baked enamel off white finish.



D.
Provide integral, gang‑operated opposed blade dampers with removable key operator, operable from face.


1.07seq level2 \h \r0 

WALL SUPPLY REGISTERS/GRILLES



A.
Streamlined and individually adjustable curved blades to discharge air along face of grille, two‑way deflection.



B.
Fabricate 1‑1/4 margin frame with concealed mounting and gasket.



C.
Fabricate of aluminum extrusions with factory off white finish.



D.
Provide integral, gang‑operated opposed blade dampers with removable key operator, operable from face.


1.08seq level2 \h \r0 

WALL EXHAUST AND RETURN REGISTERS/GRILLES



A.
Streamlined blades, depth of which exceeds 3/4 inch (19 mm) spacing, with spring or other device to set blades, vertical.



B.
Fabricate 1‑1/4 margin frame with concealed mounting.



C.
Fabricate of steel with 20 gage (0.90 mm) minimum frames and 22 gage (0.80 mm) minimum blades, steel and aluminum with 20 gage (0.90 mm) minimum frame, or aluminum extrusions, with factory baked enamel off white finish.



D.
Where not individually connected to exhaust fans, provide integral, gang‑operated opposed blade dampers with removable key operator, operable from face.



E.
In gymnasiums, blades shall be front pivoted, welded in place, or securely fastened to be immobile.

F. Provide approved Fire Marshall dampers in ducts where penetrating fire walls.

2

seq level1 \h \r0 

seq level2 \h \r0  PART 3   EXECUTION


2.01

INSTALLATION



A.
Install items in accordance with manufacturers' instructions.



B.
Check location of outlets and inlets and make necessary adjustments in position to conform with architectural features, symmetry, and lighting arrangement.  Refer to Section 09900.



C.
Install diffusers to ductwork with air tight connection.



D.
Provide balancing dampers on duct take‑off to diffusers, and grilles and registers, regardless of whether dampers are specified as part of the diffuser, or grille and register assembly.


END OF SECTION

PAGE  
Crosswinds Apartments
15936 - 1
AIR OUTLETS AND INLETS

