.

ASTM E 1300 GLASS LOAD RESISTANCE REPORT

JOB DETAILS:

Project Name:		Entrance 102 & 101 – 71” X 26.5”

WINDOW GLASS DETAILS:                         ½” Laminated Window

Lite Designation                             QTY 1   Window

Rectangular Dimensions:	Long:    71”            : Short:   26.5”

Window Construction:     	Laiminate

¼” Glass / 0.090” Clear PVB / ¼ ” Glass

Window Orientation:		Sloped at 0° from Horizontal

Product                                           ½”  Laminate

Glass Type:			Annealed

Construction:			Monolithic

Nominal Thickness:		Plate thicknesses   --  0.509”

____________________________________________________________________________

Glass Type:                                       n/a

Construction:		  	n/a

Nominal Thickness:	 	n/a

Laminate Construction:	               n/a

SHORT DURATION LOAD, RESISTANCE AND DEFLECTION DATA:

Load (<=60 sec.)    		                                            :       45 psf

Load Deflection  				               :    < 0.006     in

Maximum Allowable Glass Deflection:	:        L/175

CONCLUSION:

This glass configuration is below the maximum L/175 deflection for the specified loading.

STATEMENT OF COMPLIANCE:

Procedures followed in determining the resistance of this window glass configuration are in accordance with ASTM E 1300-97.

Disclaimer:

The load resistance of specified glass types exposed to uniform lateral loads of short or long duration subject to the following conditions:

- The glass is free of edge and surface damage and has been properly glazed in the opening in conformance with the manufacturers recommendations.

- The glass is supported on all sides by a framing system sufficiently stiff to limit lateral deflection of the glass edge (not center-of-glass) less than to 1/175 of the glass edge length; Center of glass deflection in excess of 19-mm (0.75-in.) is a design issue and does not affect glass strength;

- The laminated glass factors for short term loads are representative of roof temperature data to which the glass is exposed.

For other limiting conditions that may apply, refer to Section 5 of ASTM E1300 and local building codes.

Prepared by : 	_			___________	Date:_______6/16/2016_________