Jun 5, 2009 
P0364108 - PAGE 1

STATE OF LOUISIANA 
Department of Public Safety and Corrections 
Office of State Fire Marshal Code Enforcement and Building Safety 
8181 Independence Boulevard 
Baton Rouge, Louisiana 70806 
225-925-4920 

H “BUTCH” BROWNING 
FIRE MARSHAL 

I N F O R M A T I O N  R E Q U E S T 
N O T   -   F O R   -   P E R M I T T I N G 

	ROBERT WILTSE 
DAMMON ENGINEERING INC 
1095 FLORIDA AVE 
SLIDELL, LA  70458-0000 
	RE:  P0364108 
MIRAMON CENTER 
2515 CAREY 
SLIDELL, LA  70458-0000 

NFPA 101, 2006 

DORMITORY 



Dear Applicant: 

Additional information is required to perform a proper review.  The project referenced above is being held pending submission of the following information: 

1.        13:11.2.3.1.4 ( 3 )   Unless the requirements of 11.2.3.1.4 ( 4 ) are met for buildings having unsprinklered combustible concealed spaces, as described in 8.15.1.1 and 8.15.6, the minimum area of sprinkler operation for that portion of the building shall be 3000 sq ft.   

It appears that the unsprinklered combustible concealed space created by the plywood ceiling would require 3000 sq ft design areas for the adjacent sprinklered areas. 

2.        13:7.6.1.1  The use of antifreeze solutions shall be in conformity with state and local health regulations 

( Many local regulations require antifreeze systems to be equipped with a reduced-pressure zone backflow prevention device to guard against potential contamination of the public water supply. ) 
  

3.        13:8.6.2.2.1  The maximum allowable protection area of coverage for a sprinkler (As) shall be in accordance with the value indicated in  Table 8.6.2.2.1(a) through  Table 8.6.2.2.1(d). 

E.G., Sprinkler spacing of 144 sq ft noted in area designated as NEW STORAGE AREA; attic sprinklers also appear overspaced - see area with 11'-1" dimension between branch lines. 

4.        13:8.6.3.2.4  The requirements of  8.6.3.2.1 shall not apply within small rooms as defined in  3.3.20, sprinklers shall be permitted to be located not more than 9 ft (2.7 m) from any single wall, and sprinkler spacing limitations of  8.6.3 and area limitations of  Table 8.6.2.2.1(a) shall not be exceeded. 

The submittal is deficient in one or more of the following aspects : 

     a.      Spacing from wall exceeds 9 ft 
     b.      Spacing is more than 7-1/2 ft from more than 1 wall per room 
     c.      13:8.6.3.2.4 applied to an area(s) that does not meet the NFPA 13 definition of small room 

             13:3.3.15  Small Rooms. A room of light hazard occupancy classification having unobstructed construction and floor areas not exceeding 800 ft2 (74.3 m2) that are enclosed by walls and a ceiling. Openings in walls not exceeding 8 ft ( 2.44 m ) in width to the adjoining space are permitted if the minimum lintel depth is 8 in. (203 mm) from the ceiling.  A single opening of 36 in. ( 914 ) or less in width without a lintel is permitted when there are no other openings to adjoining spaces. 

See pendent sprinkler in the 30 bed room, to the right of node 2nd 

5.        NOTE: Please enclose a copy of this letter with future submittals or other correspondence pertaining to this project. 


Due to the lack of information, the referenced project has NOT been reviewed.  Please direct the requested information to my attention.  Processing will continue upon receipt of the information requested above.  Enclose a copy of this letter with future submittals and/or other correspondence pertaining to this project. 

This project will be returned as "NOT IN COMPLIANCE" if the requested information is not received by this office within 21 days of the date of this letter, thereby requiring a RESUBMITTAL of the entire project along with a new completed application and appropriate review fee. 

CONSTRUCTION IS NOT AUTHORIZED until a satisfactory review has been performed and a formal review letter has been issued by this office. 

REVIEWED BY: 
DONNA LEBLANC 
MECHANICAL ENGINEER 


CC: 
Rev Gene Wellington 
Jefferson Sprinkler, Inc 
Property Insurance Association* 
St Tammany Fire Protection District No 1* 
City Of Slidell* 
New Orleans District*     5042194600
