TO: Michael McLean, Plan review

FROM: Brandon Nowakowski

DATE: Oct. 31, 2007

SUBJECT: El-Bethel Church; PO334425

Dear Mr. McLean,

In your review letter for El-Bethel Church comment #15b states that:


Corridors shall be separated by minimum 1-hour fire-resistance rated fire 


partitions complying with Section 708, per IBC section 1017.

However, the building is being provided with an automatic sprinkler system; eliminating the requirement for fire-rated corridors in building occupancy group A-3. 

I am requesting that the review letter be amended to eliminate the requirement set forth in comment #15b.

Thank you,

Brandon Nowakowski

Dammon Engineering

1095 Florida Ave. 

Slidell, LA 70458

985-649-5832

