Dammon Engineering, Inc.

dammonengineering.com


1095 Florida Ave.


P.O. Box 2830



   985-649-5832

Slidell, LA 70458


Slidell, LA  70459

        FAX 985-641-5950

September 23, 2009

Mr. Lawrence Dulaune

Office of State Fire Marshal

8181 Independence Blvd.

Baton Rouge, LA 70806

RE:  
P0368920


Northshore Church


300 Kensington Ave


Slidell, LA 70458

Dear Mr. Delaune,

With regard to the above referenced project.  Prior to Dammon Engineering taking over as POR, there was an issue raised with the amount of square footage on the mezzanine.  This issued was resolved by eliminating one of the offices on the mezzanine.  

The references for a mezzanine are IBC 505.2 Exception 2 and  NFPA 8.6.9.2.1.  

We have since revised the floor plan to show the aggregate area of the mezzanine to include all existing square footage.  The floor plan has been revised to include a corridor at the bottom of the staircase from the mezzanine.  This new corridor provides access directly to Worship Center.  This revision has changed the definition for this site of the room which this mezzanine opens to.  The new nearest room that this space opens to is the Worship Center.  The Worship Center square footage is 7396 s.f. Therefore the maximum size mezzanine is  2,465 s.f.  The maximum common path of travel is 69'-3” and at this point there are two egress routes.

If you have any questions, please feel free to call.

Sincerely,

David Dammon

Project Manager

