STATE OF LOUISIANA
Department of Public Safety and Corrections
Office of State Fire Marshal Code Enforcement and Building Safety
8181 Independence Boulevard
Baton Rouge, Louisiana 70806
225-925-4920

H “BUTCH” BROWNING
FIRE MARSHAL

AMENDED LETTER

ROBERT WILTSE
DAMMON ENGINEERING INC
554 OLD SPANISH TRAIL
SLIDELL, LA  70458-0000	RE:  P0417232
JOURNEY FELLOWSHIP CHURCH
3127 PONTCHARTRIAN DR
SLIDELL, LA  70458-0000

NFPA 101, 2009 
IBC, 2009 (CHAPTERS 9 & 10)

ASSEMBLY 300 OCCUPANTS OR LESS
BUSINESS
	
Dear Applicant:

This is to advise that the previous review letter dated 07/13/2012 for this project is hereby amended as follows:

1.	Preface item 4 with the following:

If a fire alarm system is provided, ....  

Note: System is not required unless the occupant load is 300 or more persons. 

2.	Replace item 8. a) of the original review letter with the following:

	a)  No apparent requirements.

Note: IBC Table 1018.1 does not require a fire-resistance rating with sprinkler protection. 

3.	Replace item 12. a) with the following:

	a)  Comply with the "intent of the respective International Mechanical Code provisions" per IEBC Section 909.  The minimum outdoor airflow rate shall be determined in accordance with Section IMC 403.3, or demonstrate that the ventilation system design will prevent the maximum concentration of contaminents from exceeding that obtainable by the rate of outdoor air ventilation determined in accordance with Section 403.3 (IMC 403.2 Exception). 

This review applies to the work indicated on the drawings or specifications.

This review shall in no way permit or authorize any omissions or deviations from the specific requirements of the adopted codes, rules and regulations in accordance with R.S. 40:1574.1(B).

The above amended review is valid if construction starts within 180 days from the above date of the original review letter.

Occupancy of the project will not be permitted until we receive the completed certificate and a satisfactory inspection of the completed construction has been made by this office.

To arrange for inspection of the project, please contact the District Office at the phone number below, two (2) to three (3) weeks in advance. Approved plans must be available on job site at time of inspection. Certificate of completion must be provided to inspecting Deputy for final inspection.

REVIEWED BY:
LAWRENCE DELAUNE
ARCHITECT SUPERVISOR

CC:
Journey Fellowship Church
St Tammany Fire Protection District No 1*
City Of Slidell*
New Orleans District*     5045688506
City Of Slidell*
St Tammany Fire District #1*