
STANDARD
1 Aug 1998
03210
UPDATES  -



SECTION  03210


CONCRETE REINFORCING STEEL
PART 1 GENERAL
 1.1
SUMMARY
A.
Includes But Not Limited To

1.
Furnishing and installing reinforcing as described in Contract Documents.

 1.2
REFERENCES
Delete or add references based on editing of other parts of this Section.

A.
American Society For Testing And Materials
ASTM
1.
ASTM A 615-96a, 'Standard Specification for Deformed and Plain Billet-Steel Bars for Concrete Reinforcement'

Article ‘1.3' may be deleted if only a minor amount of reinforcing is being used.

 1.3
SUBMITTALS
A.
Quality Assurance / Control
Quality
1.
Provide reinforcing placement drawings.

2.
Provide mill certificates.

 1.4
DELIVERY, STORAGE, AND HANDLING
Delivery
A.
Reinforcing steel shall be free of heavy rust scales and flakes, or other coating at time of delivery and placing.  Properly protect rebar on site after delivery.  Bars shall not be stored in contact with the ground.

Paragraph ‘B’ may not be necessary if only a small amount of reinforcing is being used.

B.
Deliver bars separated by size and tagged with manufacturer's heat or test identification number.

PART 2 PRODUCTS
 2.1
MATERIAL
A.
Reinforcing Steel

1.
Rebars shall have grade identification marks and conform to ASTM A 615.

a.
Grade 60 minimum, except dowels which are to be field bent Grade 40 minimum.

b.
Bars shall be deformed type.

c.
Bars shall be free of heavy rust scales and flakes, or other bond-reducing coatings.

Rebar spacing blocks are normally used only for reinforced slab-on-grade work.

B.
Rebar Spacing Blocks

1.
Acceptable Manufactured Types -
Approved Products
a.
Single cover Frank bar chair with wire by Rebar Couplerbox Inc, Humble, TX  (713) 446-8734

b.
Equals as approved by Architect before installation.  See Section 01600.

2.
Other Approved Types -

a.
Plain concrete blocks with pre-installed wire ties.

 2.2
FABRICATION
A.
Fabricate reinforcing steel according to 'ACI Detailing Manual,' 1988 edition, and details on Drawings.

PART 3 EXECUTION
 3.1
INSTALLATION
Installation
Edit Paragraph ‘A’ to fit Project requirements.  If the concrete cover tolerances are included in a schedule on the Drawings, delete Paragraph ‘A’.

A.
Site Tolerances

1.
Provide following minimum concrete cover for reinforcement (ACI 318‑)  ‑

a.
Concrete cast against and permanently exposed to earth -

1)
Exterior Slabs on Grade (where shown)  -  2 inches

2)
Interior Slabs on Grade  -  2 inches

3)
Sections other than Slabs  -  3 inches

b.
Concrete Exposed to Earth or Weather  -

1)
No. 6 and Larger Bars  -  2 inches

2)
No. 5 and Smaller Bars  -  1-1/2 inches

Paragraph ‘1,c’ should be included on Projects with poured-in-place concrete structural elements, such as the Legacy Platform floor.  If used, edit paragraph ‘c’ to fit Project requirements.

c.
Concrete not exposed to weather or in contact with ground  -

1)
Slabs, Walls, and Joists  -  3/4 inches

2)
Beams and Columns  -

Primary Reinforcement, Ties, Stirrups, and Spirals  -  1-1/2 inches

B.
Bend bars cold.

C.
Accurately place and support with chairs, bar supports, spacers, or hangers as recommended by 'ACI Detailing Manual,' latest edition, except slab on grade work.  Support bars in slabs on grade and footings with specified rebar spacing blocks around the perimeter and 4-1/2 feet on center each way maximum to maintain specified concrete cover.  Install spacer blocks at bar intersections.

Edit Paragraph ‘D’ as required to meet Project requirements.

D.
Dowel vertical reinforcement for formed concrete columns or walls out of footing or structure below with rebar of same size and spacing required above.

E.
Securely anchor and tie reinforcing bars and dowels prior to placing concrete.

F.
Avoid splices of reinforcing bars at points of maximum stress.  Lap bars 40 bar diameters minimum unless dimensioned otherwise on the Drawings.

G.
Run steel reinforcing bars continuous through cold joints.


END OF SECTION

ADVANCE \d252
B L A N K   P A G E

557-1804 (20020)
1
Section 03210

Orlando Welfare Complex

Concrete Reinforcing Steel


