STATE OF LOUISIANA
Department of Public Safety and Corrections
Office of State Fire Marshal Code Enforcement and Building Safety
8181 Independence Boulevard
Baton Rouge, Louisiana 70806
225-925-4920

HENRY H. FRY
DEPUTY ASSISTANT SECRETARY

AMENDED LETTER

EMMETT DAMMON, P.E., E.E.
DAMMON ENGINEERING
1095 FLORIDA AVE
SLIDELL, LA  70458-0000	RE:  P0299640
MAURIN WAREHOUSE
43270 AIRPORT RD
HAMMOND, LA  70404-0000

NFPA 101, 2003

INDUSTRIAL
BUSINESS
	
Dear Applicant:

This is to advise that the previous review letter dated 10/04/2005 for this project is hereby amended as follows:

1.	Our review of drawings and/or specifications for the subject project dated as indicated above is amended as follows:

     a. Occupancy was incorrectly noted on original review letter. Occupancy is mixed Industrial/business occupancy.

    b. Per 6.1.14.1.3(3) a separation is not required when the business part is less than 25% of the total square footage. Building appears to comply with this requirement.

    c. All other items cited in original review letter are to remain in effect. 

2.	NOTE: Please enclose a copy of this letter with future submittals or other correspondence pertaining to this project. 

This review applies to the work indicated on the drawings or specifications.

This review shall in no way permit or authorize any omissions or deviations from the specific requirements of the adopted codes, rules and regulations in accordance with R.S. 40:1574.1(B).

The above amended review is valid if construction starts within 180 days from the above date of the original review letter.

Occupancy of the project will not be permitted until we receive the completed certificate and a satisfactory inspection of the completed construction has been made by this office.

To arrange for inspection of the project, please contact the District Office at the phone number below, two (2) to three (3) weeks in advance. Approved plans must be available on job site at time of inspection. Certificate of completion must be provided to inspecting Deputy for final inspection.

REVIEWED BY:
LINDA BURCH
PLAN REVIEW DEPUTY

CC:
Jamestown Inc
Alyson Lapuma*
Hammond Fire Prevention Bureau*
Hammond Building Inspector*
Baton Rouge District*     2259253650