[image: image1.png]


554 Old Spanish Trail

Slidell, LA 70458

Phone: 985-649-5832

Fax: 985-641-5950

dammonengineering.com

dammoneng@bellsouth.net


June 27, 2013
Zachary Smith
Plan Reviewer
Department of Safety and Permits

1300 Perdido Street Suite 7E06
New Orleans, LA  70112
Re:  
13-18181 – 8338 Oak St.

Dear Mr. Smith,
Please see our responses below to your questions on the above referenced building plans:
ARCHITECTURAL

1. Acknowledged.

2. Acknowledged.
3. Approval letter from the Office of State Fire Marshal is enclosed.
4. Drawings will be submitted to the Orleans Parish Sanitary Services for approval.

5. The Department of Property Management will be contacted regarding outward swinging doors and the new ramp for approval.

6. The Department of Public Works will be contacted regarding the new ramp on sidewalk for approval.
7. Per Table 1014.3, the maximum common path of travel for Business Occupancy with an occupant load of greater than 30 is 75’.  However, where the occupant load is 30 or less, the maximum common path of travel is 100’.  The occupant load for the portion of the building identified as Business occupancy is 28.  Therefore the maximum common path of travel of 87’ does not exceed that allowed.
8. Refer to attached site plan.

9. The second floor storage area was originally the warehouse for the hardware store that previously occupied the building.  The owner of the building intends to maintain that space for storage of the same materials that were stored while the hardware store was in operation.  All materials stored are non-combustable in nature, however, many are contained in cardboard boxes which would require that the hazard classification be ordinary hazard.  There is no planned occupancy for this space.
10. Openings in fire-rated walls, barriers, and partitions will be in accordance with Section 715 of the IBC 2009 ed.  Doors in 2-hour rated wall will have a required fire-rating of 90 minutes.
11. The fire rating separating the second floor storage area from the business occupancy below will be 2-hours.
12. Egress doors will comply with Section 1008.1.9 IBC 2009 ed.

13. Individual glazed areas in hazardous locations will comply with Section 2406.4 IBC 2009 ed.

14. All areas that are prone to exposure to water (toilets, bathing, etc.) will be of the proper materials as specified in Section 1210 IBC 2009 ed.

MECHANICAL

1. New A/C systems shall tie into the new floor drain in the Mechanical Room as shown on P2.  These are vertical units and specification data and details will be supplied to the contractor/owner.
2. Regarding the second floor mechanical (hvac) work, the storage area is currently unconditioned and is planned to remain so.  The residential portion of the second floor is currently conditioned but the limits of the hvac work in this area is confined to repair/replacement of existing non-functioning equipment by the owner and is not part of this scope of work.
Please find attached a copy of your review letter dated June 19, 2013, a copy of the State Fire Marshal approval letter, and the site plan.  If you have any additional questions please do not hesitate to contact me.
Sincerely,
[image: image2.jpg]IDAMMON

ENGINEERING | NLC.

J  Archiltectls & Engineers





Kevin J. Kinchen
Chief Architect
Enclosures

Cc:
Randy Broussard


Dragan Segvic

Emily Johnston
