
[image: image1.wmf]The information on this

document is created by Eaton

Corporation. It is disclosed

in confidence and it is only

to be used for the purpose in

which it is supplied.

PREPARED BY

DeepaMManjarekar

DATE

08/20/13

APPROVED BY

DATE

VERSION

7.9

NEG-ALT NUMBER

LT520529W305-C000

REVISION

DWG SIZE

A

Eaton Corporation

Fayetteville, NC

JOB NAME

Sunbelt Carwash

DESIGNATION

RAINFOREST

TYPE

MCC 2100

DRAWING TYPE

Customer Appr.

G.O.

SMO0430798

ITEM

002

SHEET

1 OF 7

MCC General Information

MCC General Information

Wiring Diagram Type

C-H Standard

MCC Quantity

1

Standards

UL845, NEMA, NEC

Special Codes

UL

Service Voltage (3 Phase)

480V

Frequency

60 Hz

System

3PH4W

Enclosure Specifications

Total Structures

7

Type

NEMA 1 Gasketed

Depth

21" Front Mt Only

Height

90"

Horizontal Wireways

9" High, Top & Bottom

Vertical Wireways

4"

Channel Sills

Yes

Bottom Plates

No

150 Watt Space Heaters

None

Space Heater Thermostat

No

Master Terminal Block Location

None

IBC/CBC Seismic Qualified

No

Bus System Specifications

Main Bus Amps

600A

Main Bus Material

Copper

Main Bus Bar Plating

Tin

Insulated Horiz. Bus

No

1000A/sq in. Cu Bus

No

Vertical Bus Amps

See Structure Schedule

Vertical Bus Material

Tin Plated Copper

Vertical Bus Barrier

Labyrinth, Isolated/Insulated with shutters

Bus Bracing

42,000

Ground Bus

300

Ground Bus Location

Top

Ground Bus Lug Size

1-#6-350Kcmil

Ground Bus Lug Type

Screw

Plug-in 300A Vert. Gnd. Bus

No

Neutral

300A

Neutral Bus Lug Location

Incoming Line

Neutral Bus Lug Size

1-#6-350Kcmil

Neutral Bus Lug Type

Screw

Horizontal Bus Temperature Rise

65 deg C

Bottom Vert. Bus Barrier

No

Vertical Ground Bus

No

Incoming Line Termination

Device: #4-350 Kcmil 4/Ph  Main Lugs (Screw)

Cable Entry

Top

Splice Kit / Transition

None

MCC Type Match Up

MCC Type Match Up GO#

** None **

MCC Starter Specifications

Wiring Class

1B

Control Voltage

120V

Control Voltage Src

Ind CPT

Nameplate Size

1" X 2.5"

Nameplate Color

Black / White Letters

Pilot Dev. Model

10250T

Ind. Light Type

6v Xfmr

PL Color (On)

Red

Structure Schedule

There are 7 structure(s).

All structures have a 600 A vertical bus.

Total width of all sections is 140.0"

Height of all sections is 91"

Unit Modifications

Solid State Overload Relay (Standard)

Terminal Block - Latching Pull-Apart, Std.

#16awg, MTW Control Wire


[image: image2.wmf]The information on this

document is created by Eaton

Corporation. It is disclosed

in confidence and it is only

to be used for the purpose in

which it is supplied.

PREPARED BY

DeepaMManjarekar

DATE

08/20/13

APPROVED BY

DATE

VERSION

7.9

NEG-ALT NUMBER

LT520529W305-C000

REVISION

DWG SIZE

A

Eaton Corporation

Fayetteville, NC

JOB NAME

Sunbelt Carwash

DESIGNATION

RAINFOREST

TYPE

MCC 2100

DRAWING TYPE

Customer Appr.

G.O.

SMO0430798

ITEM

002

SHEET

2 OF 7

MLO

FVNR S2

FVNR S2

FVNR S2

FVNR S2

FVNR S2

FVNR S2

FVNR S2

FVNR S2

FVNR S2

FVNR S2

FVNR S1

FVNR S1

FVNR S1

FVNR S1

FVNR S1

FVNR S1

FVNR S2

FVNR S1

FVNR S1

FVNR S1

FVNR S1

FVNR S1

1F

A

B

C

D

E

F

G

H

J

K

L

M

5.41"

17.50"

1.00"

1.25"

20.0"

21.00"

Floor View

5.41"

17.50"

Top View

2F

5.41"

17.50"

1.00"

1.25"

20.0"

5.41"

17.50"

3F

5.41"

17.50"

1.00"

1.25"

20.0"

5.41"

17.50"

4F

5.41"

17.50"

1.00"

1.25"

20.0"

5.41"

17.50"


[image: image3.wmf]The information on this

document is created by Eaton

Corporation. It is disclosed

in confidence and it is only

to be used for the purpose in

which it is supplied.

PREPARED BY

DeepaMManjarekar

DATE

08/20/13

APPROVED BY

DATE

VERSION

7.9

NEG-ALT NUMBER

LT520529W305-C000

REVISION

DWG SIZE

A

Eaton Corporation

Fayetteville, NC

JOB NAME

Sunbelt Carwash

DESIGNATION

RAINFOREST

TYPE

MCC 2100

DRAWING TYPE

Customer Appr.

G.O.

SMO0430798

ITEM

002

SHEET

3 OF 7

FVNR S1

FVNR S1

FVNR S2

42CKT

RLY PNL

5F

A

B

C

D

E

F

G

H

J

K

L

M

5.41"

17.50"

1.00"

1.25"

20.0"

21.00"

Floor View

5.41"

17.50"

Top View

6F

5.41"

17.50"

1.00"

1.25"

20.0"

5.41"

17.50"

7F

5.41"

17.50"

1.00"

1.25"

20.0"

5.41"

17.50"


[image: image4.wmf]The information on this

document is created by Eaton

Corporation. It is disclosed

in confidence and it is only

to be used for the purpose in

which it is supplied.

PREPARED BY

DeepaMManjarekar

DATE

08/20/13

APPROVED BY

DATE

VERSION

7.9

NEG-ALT NUMBER

LT520529W305-C000

REVISION

DWG SIZE

A

Eaton Corporation

Fayetteville, NC

JOB NAME

Sunbelt Carwash

DESIGNATION

RAINFOREST

TYPE

MCC 2100

DRAWING TYPE

Customer Appr.

G.O.

SMO0430798

ITEM

002

SHEET

4 OF 7

Unit

Nameplate

Description

Class 

Starter Size

Bkr/Sw

Unit

HP/FLA

Poles

Features

Wire Diag.

Trip/Clip

1C

#4-350 Kcmil 4/Ph 

Main Lugs (Screw)

1E

FVNR Starter Size 2

F206

2

HMCP

[HMCP]

25

3P

70

265744.DWF

1

100VA Individual CPT, Fused

1

N.O. Starter Aux Contacts, Size 1-4

1

Pilot Light-10250T (Run)

1

3 Pos. Sel. Sw., 10250T (Hand-Off-Auto)

BELANGER BLOWERS

1G

FVNR Starter Size 2

F206

2

HMCP

[HMCP]

25

3P

70

265744.DWF

1

100VA Individual CPT, Fused

1

N.O. Starter Aux Contacts, Size 1-4

1

Pilot Light-10250T (Run)

1

3 Pos. Sel. Sw., 10250T (Hand-Off-Auto)

BELANGER BLOWERS

1J

FVNR Starter Size 2

F206

2

HMCP

[HMCP]

25

3P

70

265744.DWF

1

100VA Individual CPT, Fused

1

N.O. Starter Aux Contacts, Size 1-4

1

Pilot Light-10250T (Run)

1

3 Pos. Sel. Sw., 10250T (Hand-Off-Auto)

BELANGER BLOWERS

1L

FVNR Starter Size 2

F206

2

HMCP

[HMCP]

25

3P

70

265744.DWF

1

100VA Individual CPT, Fused

1

N.O. Starter Aux Contacts, Size 1-4

1

Pilot Light-10250T (Run)

1

3 Pos. Sel. Sw., 10250T (Hand-Off-Auto)

SONNYS VAC

1M

6" Door

2B

FVNR Starter Size 2

F206

2

HMCP

[HMCP]

15

3P

50

265744.DWF

1

100VA Individual CPT, Fused

1

N.O. Starter Aux Contacts, Size 1-4

1

Pilot Light-10250T (Run)

1

3 Pos. Sel. Sw., 10250T (Hand-Off-Auto)

SONNYS VAC

2D

FVNR Starter Size 2

F206

2

HMCP

[HMCP]

15

3P

50

265744.DWF

1

100VA Individual CPT, Fused

1

N.O. Starter Aux Contacts, Size 1-4

1

Pilot Light-10250T (Run)

1

3 Pos. Sel. Sw., 10250T (Hand-Off-Auto)

SONNYS VAC


[image: image5.wmf]The information on this

document is created by Eaton

Corporation. It is disclosed

in confidence and it is only

to be used for the purpose in

which it is supplied.

PREPARED BY

DeepaMManjarekar

DATE

08/20/13

APPROVED BY

DATE

VERSION

7.9

NEG-ALT NUMBER

LT520529W305-C000

REVISION

DWG SIZE

A

Eaton Corporation

Fayetteville, NC

JOB NAME

Sunbelt Carwash

DESIGNATION

RAINFOREST

TYPE

MCC 2100

DRAWING TYPE

Customer Appr.

G.O.

SMO0430798

ITEM

002

SHEET

5 OF 7

Unit

Nameplate

Description

Class 

Starter Size

Bkr/Sw

Unit

HP/FLA

Poles

Features

Wire Diag.

Trip/Clip

2F

FVNR Starter Size 2

F206

2

HMCP

[HMCP]

15

3P

50

265744.DWF

1

100VA Individual CPT, Fused

1

N.O. Starter Aux Contacts, Size 1-4

1

Pilot Light-10250T (Run)

1

3 Pos. Sel. Sw., 10250T (Hand-Off-Auto)

SONNYS VAC

2H

FVNR Starter Size 2

F206

2

HMCP

[HMCP]

15

3P

50

265744.DWF

1

100VA Individual CPT, Fused

1

N.O. Starter Aux Contacts, Size 1-4

1

Pilot Light-10250T (Run)

1

3 Pos. Sel. Sw., 10250T (Hand-Off-Auto)

SONNYS BLOWERS

2K

FVNR Starter Size 2

F206

2

HMCP

[HMCP]

15

3P

50

265744.DWF

1

100VA Individual CPT, Fused

1

N.O. Starter Aux Contacts, Size 1-4

1

Pilot Light-10250T (Run)

1

3 Pos. Sel. Sw., 10250T (Hand-Off-Auto)

 SONNYS BLOWERS

2M

FVNR Starter Size 2

F206

2

HMCP

[HMCP]

15

3P

50

265744.DWF

1

100VA Individual CPT, Fused

1

N.O. Starter Aux Contacts, Size 1-4

1

Pilot Light-10250T (Run)

1

3 Pos. Sel. Sw., 10250T (Hand-Off-Auto)

SONNYS BLOWERS

3B

FVNR Starter Size 1

F206

1

HMCP

[HMCP]

7.5

3P

30

265744.DWF

1

100VA Individual CPT, Fused

1

N.O. Starter Aux Contacts, Size 1-4

1

Pilot Light-10250T (Run)

1

3 Pos. Sel. Sw., 10250T (Hand-Off-Auto)

WRAP 1

3D

FVNR Starter Size 1

F206

1

HMCP

[HMCP]

7.5

3P

30

265744.DWF

1

100VA Individual CPT, Fused

1

N.O. Starter Aux Contacts, Size 1-4

1

Pilot Light-10250T (Run)

1

3 Pos. Sel. Sw., 10250T (Hand-Off-Auto)

WRAP 2

3F

FVNR Starter Size 1

F206

1

HMCP

[HMCP]

7.5

3P

30

265744.DWF

1

100VA Individual CPT, Fused

1

N.O. Starter Aux Contacts, Size 1-4

1

Pilot Light-10250T (Run)

1

3 Pos. Sel. Sw., 10250T (Hand-Off-Auto)

CONVEYOR

3H

FVNR Starter Size 1

F206

1

HMCP

[HMCP]

7.5

3P

30

265744.DWF

1

100VA Individual CPT, Fused

1

N.O. Starter Aux Contacts, Size 1-4

1

Pilot Light-10250T (Run)

1

3 Pos. Sel. Sw., 10250T (Hand-Off-Auto)

CONVEYOR


[image: image6.wmf]The information on this

document is created by Eaton

Corporation. It is disclosed

in confidence and it is only

to be used for the purpose in

which it is supplied.

PREPARED BY

DeepaMManjarekar

DATE

08/20/13

APPROVED BY

DATE

VERSION

7.9

NEG-ALT NUMBER

LT520529W305-C000

REVISION

DWG SIZE

A

Eaton Corporation

Fayetteville, NC

JOB NAME

Sunbelt Carwash

DESIGNATION

RAINFOREST

TYPE

MCC 2100

DRAWING TYPE

Customer Appr.

G.O.

SMO0430798

ITEM

002

SHEET

6 OF 7

Unit

Nameplate

Description

Class 

Starter Size

Bkr/Sw

Unit

HP/FLA

Poles

Features

Wire Diag.

Trip/Clip

3K

FVNR Starter Size 1

F206

1

HMCP

[HMCP]

5

3P

15

265744.DWF

1

100VA Individual CPT, Fused

1

N.O. Starter Aux Contacts, Size 1-4

1

Pilot Light-10250T (Run)

1

3 Pos. Sel. Sw., 10250T (Hand-Off-Auto)

NINJA

3M

FVNR Starter Size 1

F206

1

HMCP

[HMCP]

7.5

3P

30

265744.DWF

1

100VA Individual CPT, Fused

1

N.O. Starter Aux Contacts, Size 1-4

1

Pilot Light-10250T (Run)

1

3 Pos. Sel. Sw., 10250T (Hand-Off-Auto)

BISON/18"

4B

FVNR Starter Size 2

F206

2

HMCP

[HMCP]

15

3P

50

265744.DWF

1

100VA Individual CPT, Fused

1

N.O. Starter Aux Contacts, Size 1-4

1

Pilot Light-10250T (Run)

1

3 Pos. Sel. Sw., 10250T (Hand-Off-Auto)

OMNI TOP PUMP

4D

FVNR Starter Size 1

F206

1

HMCP

[HMCP]

10

3P

30

265744.DWF

1

100VA Individual CPT, Fused

1

N.O. Starter Aux Contacts, Size 1-4

1

Pilot Light-10250T (Run)

1

3 Pos. Sel. Sw., 10250T (Hand-Off-Auto)

BUFF N DRY

ELEPHANT EAR

BLOWERS

4F

FVNR Starter Size 1

F206

1

HMCP

[HMCP]

10

3P

30

265744.DWF

1

100VA Individual CPT, Fused

1

N.C. Starter Aux Contacts, Size 1-4

1

N.O. Starter Aux Contacts, Size 1-4

1

Pilot Light-10250T (Run)

1

3 Pos. Sel. Sw., 10250T (Hand-Off-Auto)

BUFF N DRY

ELEPHANT EAR

BLOWERS

4H

FVNR Starter Size 1

F206

1

HMCP

[HMCP]

10

3P

30

265744.DWF

1

100VA Individual CPT, Fused

1

N.C. Starter Aux Contacts, Size 1-4

1

N.O. Starter Aux Contacts, Size 1-4

1

Pilot Light-10250T (Run)

1

3 Pos. Sel. Sw., 10250T (Hand-Off-Auto)

BUFF N DRY

ELEPHANT EAR

BLOWERS

4K

FVNR Starter Size 1

F206

1

HMCP

[HMCP]

10

3P

30

265744.DWF

1

100VA Individual CPT, Fused

1

N.C. Starter Aux Contacts, Size 1-4

1

N.O. Starter Aux Contacts, Size 1-4

1

Pilot Light-10250T (Run)

1

3 Pos. Sel. Sw., 10250T (Hand-Off-Auto)

PREP GUN

4M

FVNR Starter Size 1

F206

1

HMCP

[HMCP]

10

3P

30

265744.DWF

1

100VA Individual CPT, Fused

1

N.C. Starter Aux Contacts, Size 1-4

1

N.O. Starter Aux Contacts, Size 1-4

1

Pilot Light-10250T (Run)

1

3 Pos. Sel. Sw., 10250T (Hand-Off-Auto)

AIR 

COMPRESSOR 1


[image: image7.wmf]The information on this

document is created by Eaton

Corporation. It is disclosed

in confidence and it is only

to be used for the purpose in

which it is supplied.

PREPARED BY

DeepaMManjarekar

DATE

08/20/13

APPROVED BY

DATE

VERSION

7.9

NEG-ALT NUMBER

LT520529W305-C000

REVISION

DWG SIZE

A

Eaton Corporation

Fayetteville, NC

JOB NAME

Sunbelt Carwash

DESIGNATION

RAINFOREST

TYPE

MCC 2100

DRAWING TYPE

Customer Appr.

G.O.

SMO0430798

ITEM

002

SHEET

7 OF 7

Unit

Nameplate

Description

Class 

Starter Size

Bkr/Sw

Unit

HP/FLA

Poles

Features

Wire Diag.

Trip/Clip

5B

FVNR Starter Size 1

F206

1

HMCP

[HMCP]

5

3P

15

265744.DWF

1

100VA Individual CPT, Fused

1

N.O. Starter Aux Contacts, Size 1-4

1

Pilot Light-10250T (Run)

1

3 Pos. Sel. Sw., 10250T (Hand-Off-Auto)

REPRESSURIZATION

PUMP

5D

FVNR Starter Size 1

F206

1

HMCP

[HMCP]

5

3P

15

265744.DWF

1

100VA Individual CPT, Fused

1

N.O. Starter Aux Contacts, Size 1-4

1

Pilot Light-10250T (Run)

1

3 Pos. Sel. Sw., 10250T (Hand-Off-Auto)

AIR

COMPRESSION

5F

FVNR Starter Size 2

F206

2

HMCP

[HMCP]

15

3P

50

265744.DWF

1

100VA Individual CPT, Fused

1

N.O. Starter Aux Contacts, Size 1-4

1

Pilot Light-10250T (Run)

1

3 Pos. Sel. Sw., 10250T (Hand-Off-Auto)

OMNI SIDE PUMP

5H

12" Door

5K

12" Door

5M

12" Door

6B

12" Door

6M

PL3A Panelboard

250A 277/480V 3PH

4W 42 CKT

1

Pnlbd Bkr, EHD 3 Pole 20A bkr

6

Pnlbd Bkr, EHD 1 Pole 15A bkr

7

Pnlbd Bkr, EHD 3 Pole 15A bkr

3

Pnlbd Bkr, EHD 3 Pole 30A bkr

1

Pnlbd Bkr, EHD 3 Pole 50A bkr

7M

72 in. blank relay

panel

1

Pilot Light-10250T (Run)

1

3 Pos. Sel. Sw., 10250T (Hand-Off-Auto)


 7
Adjustable Frequency Drives



Catalog Number: MMX34AA2D4F0-0

MMX Series, 480VAC Three Phase, 1 HP, FLA: 2.4, Enclosure: MMX NEMA TYPE 0  (No Filter)

GLOBAL LIST OF MATERIAL:

Base Drive Catnum: MMX34AA2D4F0-0


 1           M-MAX 3P 480V IN / 3P 480V OUT, 2.4A, 1.0HP, FS1, W EMC


Drawings Numbers: 

Designations: 
Drive


1
Freedom MCC
60 Hz, Class 1B wiring, 480V 3-Phase Service, 42,000 Bracing, Top Incoming,
NEMA 1 Gasketed 21" Front Mt Only enclosure, 600A Copper Main Horizontal Bus,
ANeutral, Main Lugs



1
#4-350 Kcmil 4/Ph  Main Lugs (Screw)

13
FVNR Starter Size 1 [HMCP]

12
FVNR Starter Size 2 [HMCP]

25
100VA Individual CPT, Fused

4
N.C. Starter Aux Contacts, Size 1-4

25
N.O. Starter Aux Contacts, Size 1-4

26
Pilot Light-10250T (Run)

25
Solid State Overload Relay (Standard)

26
3 Pos. Sel. Sw., 10250T (Hand-Off-Auto)

25
Terminal Block - Latching Pull-Apart, Std.

25
#16awg, MTW Control Wire

1
PL3A Panelboard 250A 277/480V 3PH 4W 42 CKT

7
Pnlbd Bkr, EHD 3 Pole 15A bkr

6
Pnlbd Bkr, EHD 1 Pole 15A bkr

3
Pnlbd Bkr, EHD 3 Pole 30A bkr

1
Pnlbd Bkr, EHD 3 Pole 20A bkr

1
Pnlbd Bkr, EHD 3 Pole 50A bkr

1
72 in. blank relay panel

7
Structure Floor Leveling Channel Sills

7
300A Copper Full Length Neutral Bus

7
300A Horiz. Cu Gnd Bus, 1/4" x 1" Bar

7
Labyrinth, Isolated/Insulated vertical bus barrier with shutters

7
600A Vertical Bus (Tin-plated cu)

7
42KA Bus Bracing

7
Tin Plated horizontal bus

7
600A Copper Frnt Mtd 21" NEMA 1 Gasketed

1
6" Door

4
12" Door


Special Configuration Notes:


Used X-Space:
75

Blank X-Space:
9

Future X-Space:
0

MCC Lead Time Code:
B

Designations: 
RAINFOREST



