STATE OF LOUISIANA

STATE POLICE TROOP L HEADQUARTERS

HVAC SYSTEM REPLACEMENT

MANDEVILLE, LOUISIANA



SECTION 230500
BASIC MECHANICAL MATERIALS AND METHODS
PART 1 -  GENERAL

1.1 SUMMARY

A. This Section includes the following:

1. Piping materials and installation instructions common to most piping systems.

2. Mechanical demolition.

3. Equipment installation requirements common to equipment sections.

4. Concrete bases.

5. Supports and anchorages.

1.2 DEFINITIONS

A. Finished Spaces:  Spaces other than mechanical and electrical equipment rooms, furred spaces, pipe and duct shafts, unheated spaces immediately below roof, spaces above ceilings, unexcavated spaces, crawlspaces, and tunnels.

B. Exposed, Interior Installations:  Exposed to view indoors.  Examples include finished occupied spaces and mechanical equipment rooms.

C. Exposed, Exterior Installations:  Exposed to view outdoors or subject to outdoor ambient temperatures and weather conditions.  Examples include rooftop locations.

D. Concealed, Interior Installations:  Concealed from view and protected from physical contact by building occupants.  Examples include above ceilings and in duct shafts.

E. Concealed, Exterior Installations:  Concealed from view and protected from weather conditions and physical contact by building occupants but subject to outdoor ambient temperatures.  Examples include installations within unheated shelters.

1.3 SUBMITTALS

Retain this Article if procedures for welder certification are retained in "Quality Assurance" Article.

A. Welding certificates.

1.4 QUALITY ASSURANCE

Delete first paragraph below if no welding.  AWS states that welding qualifications remain in effect indefinitely unless welding personnel have not welded for more than six months or there is a specific reason to question their ability.

A. Steel Pipe Welding:  Qualify processes and operators according to ASME Boiler and Pressure Vessel Code:  Section IX, "Welding and Brazing Qualifications."

1. Certify that each welder has passed AWS qualification tests for welding processes involved and that certification is current.

B. Electrical Characteristics for Mechanical Equipment:  Equipment of higher electrical characteristics may be furnished provided such proposed equipment is approved in writing and connecting electrical services, circuit breakers, and conduit sizes are appropriately modified.  If minimum energy ratings or efficiencies are specified, equipment shall comply with requirements.

PART 2 -  PRODUCTS

2.1 PIPE, TUBE, AND FITTINGS

A. Refer to individual sections for pipe, tube, and fitting materials and joining methods.

B. Pipe Threads:  ASME B1.20.1 for factory-threaded pipe and pipe fittings.

2.2 JOINING MATERIALS

A. Refer to individual sections for special joining materials not listed below.

B. Pipe-Flange Gasket Materials:  ASME B16.21, nonmetallic, flat, asbestos-free, 1/8-inch maximum thickness unless thickness or specific material is indicated.

C. Plastic, Pipe-Flange Gasket, Bolts, and Nuts:  Type and material recommended by piping system manufacturer, unless otherwise indicated.

D. Solder Filler Metals:  ASTM B 32, lead-free alloys.  Include water-flushable flux according to ASTM B 813.

E. Brazing Filler Metals:  AWS A5.8, BCuP Series or BAg1, unless otherwise indicated.

F. Welding Filler Metals:  Comply with AWS D10.12.

G. Solvent Cements for Joining Plastic Piping:

1. ABS Piping:  ASTM D 2235.

2. CPVC Piping:  ASTM F 493.

3. PVC Piping:  ASTM D 2564.  Include primer according to ASTM F 656.

4. PVC to ABS Piping Transition:  ASTM D 3138.

2.3 SEALS

A. Description:  Modular sealing element unit, designed for field assembly, to fill annular space between pipe and sleeve.

B. Sealing Elements:  EPDM interlocking links shaped to fit surface of pipe.  Include type and number required for pipe material and size of pipe.

2.4 SLEEVES

A. Galvanized-Steel Sheet:  0.0239-inch minimum thickness; round tube closed with welded longitudinal joint.

B. Steel Pipe:  ASTM A 53, Type E, Grade B, Schedule 40, galvanized, plain ends.

Sleeve in paragraph below is available with many end variations.

Sleeve in paragraph below is without seepage holes and cannot be used instead of a floor drain.

PVC sleeves in first two paragraphs below may be prohibited by fire authorities having jurisdiction.

C. Molded PVC:  Permanent, with nailing flange for attaching to wooden forms.

D. PVC Pipe:  ASTM D 1785, Schedule 40.

PART 3 -  EXECUTION

3.1 MECHANICAL DEMOLITION

Delete this Article if no mechanical demolition is required.  Edit this Article as required for mechanical demolition.  Show items for demolition on Drawings and supplement Drawings with descriptions in this Article.

A. Disconnect, demolish, and remove mechanical systems, equipment, and components indicated to be removed.

1. Piping to Be Removed:  Remove piping indicated to be removed and cap or plug remaining piping with same or compatible piping material.

2. Piping to Be Abandoned in Place:  Drain piping and cap or plug piping with same or compatible piping material.

3. Ducts to Be Removed:  Remove ducts indicated to be removed and plug remaining ducts with same or compatible ductwork material.

4. Ducts to Be Abandoned in Place:  Cap or plug ducts with same or compatible ductwork material.

5. Equipment to Be Removed:  Disconnect and cap services and remove equipment.

6. Equipment to Be Removed and Reinstalled:  Disconnect and cap services and remove, clean, and store equipment; when appropriate, reinstall, reconnect, and make equipment operational.

7. Equipment to Be Removed and Salvaged:  Disconnect and cap services and remove equipment and deliver to Owner.

8. Equipment to be inspected and cleaned:  Chillers, boilers, expansion tanks and appurtenances notes to be reused.  Flush with clean water and inspect for damage.  Report damages or unusual observations to Dammon Engineering for resolution.

B. If pipe, insulation, or equipment to remain is damaged in appearance or is unserviceable, remove damaged or unserviceable portions and replace with new products of equal capacity and quality.

3.2 PIPING SYSTEMS - COMMON REQUIREMENTS

A. Install piping according to the following requirements and sections specifying piping systems.

B. Drawing plans, schematics, and diagrams indicate general location and arrangement of piping systems.  Indicated locations and arrangements were used to size pipe and calculate friction loss, expansion, pump sizing, and other design considerations.  Install piping as indicated unless deviations to layout are approved on Coordination Drawings.

C. Reconnect chillers, boilers, expansion tanks and appurtenances to be reused.

D. Install piping in concealed locations, unless otherwise indicated and except in equipment rooms and service areas.

E. Install piping indicated to be exposed and piping in equipment rooms and service areas at right angles or parallel to building walls.  Diagonal runs are prohibited unless specifically indicated otherwise.

F. Install piping above accessible ceilings to allow sufficient space for ceiling panel removal.

G. Install piping to permit valve servicing.

H. Install piping at indicated slopes.

I. Install piping free of sags and bends.

J. Install fittings for changes in direction and branch connections.

K. Install piping to allow application of insulation.

L. Select system components with pressure rating equal to or greater than system operating pressure.

M. Install escutcheons for penetrations of walls, ceilings, and floors.

N. Install sleeves for pipes passing through concrete and masonry walls, gypsum-board partitions, and concrete floor and roof slabs.

O. Aboveground, Exterior-Wall Pipe Penetrations:  Seal penetrations using sleeves and mechanical sleeve seals.  Select sleeve size to allow for 1-inch annular clear space between pipe and sleeve for installing mechanical sleeve seals.

1. Install steel pipe for sleeves smaller than 6 inches in diameter.

2. Install cast-iron "wall pipes" for sleeves 6 inches and larger in diameter.

3. Mechanical Sleeve Seal Installation:  Select type and number of sealing elements required for pipe material and size.  Position pipe in center of sleeve.  Assemble mechanical sleeve seals and install in annular space between pipe and sleeve.  Tighten bolts against pressure plates that cause sealing elements to expand and make watertight seal.

Edit first paragraph below to suit Project and add description of firestopping sealant.

P. Fire-Barrier Penetrations:  Maintain indicated fire rating of walls, partitions, ceilings, and floors at pipe penetrations.  Seal pipe penetrations with firestop materials.  

Q. Verify final equipment locations for roughing-in.

R. Refer to equipment specifications in other Sections of these Specifications for roughing-in requirements.

3.3 PIPING JOINT CONSTRUCTION

A. Join pipe and fittings according to the following requirements and sections specifying piping systems.

B. Ream ends of pipes and tubes and remove burrs.  Bevel plain ends of steel pipe.

C. Remove scale, slag, dirt, and debris from inside and outside of pipe and fittings before assembly.

D. Soldered Joints:  Apply ASTM B 813, water-flushable flux, unless otherwise indicated, to tube end.  Construct joints according to ASTM B 828 or CDA's "Copper Tube Handbook," using lead-free solder alloy complying with ASTM B 32.

E. Brazed Joints:  Construct joints according to AWS's "Brazing Handbook," "Pipe and Tube" Chapter, using copper-phosphorus brazing filler metal complying with AWS A5.8.

F. Threaded Joints:  Thread pipe with tapered pipe threads according to ASME B1.20.1.  Cut threads full and clean using sharp dies.  Ream threaded pipe ends to remove burrs and restore full ID.  Join pipe fittings and valves as follows:

1. Apply appropriate tape or thread compound to external pipe threads unless dry seal threading is specified.

2. Damaged Threads:  Do not use pipe or pipe fittings with threads that are corroded or damaged.  Do not use pipe sections that have cracked or open welds.

G. Welded Joints:  Construct joints according to AWS D10.12, using qualified processes and welding operators according to Part 1 "Quality Assurance" Article.

H. Flanged Joints:  Select appropriate gasket material, size, type, and thickness for service application.  Install gasket concentrically positioned.  Use suitable lubricants on bolt threads.

I. Plastic Piping Solvent-Cement Joints:  Clean and dry joining surfaces.  Join pipe and fittings according to the following:

1. Comply with ASTM F 402, for safe-handling practice of cleaners, primers, and solvent cements.

2. ABS Piping:  Join according to ASTM D 2235 and ASTM D 2661 Appendixes.

3. CPVC Piping:  Join according to ASTM D 2846/D 2846M Appendix.

4. PVC Pressure Piping:  Join schedule number ASTM D 1785, PVC pipe and PVC socket fittings according to ASTM D 2672.  Join other-than-schedule-number PVC pipe and socket fittings according to ASTM D 2855.

5. PVC Nonpressure Piping:  Join according to ASTM D 2855.

6. PVC to ABS Nonpressure Transition Fittings:  Join according to ASTM D 3138 Appendix.

J. Plastic Pressure Piping Gasketed Joints:  Join according to ASTM D 3139.

K. Plastic Nonpressure Piping Gasketed Joints:  Join according to ASTM D 3212.

3.4 PIPING CONNECTIONS

A. Make connections according to the following, unless otherwise indicated:

1. Install unions, in piping NPS 2 and smaller at final connection to each piece of equipment.

2. Install flanges, in piping NPS 2-1/2 and larger, adjacent to flanged valves and at final connection to each piece of equipment.

Edit dielectric connection types in two subparagraphs below for each fluid.

3.5 EQUIPMENT INSTALLATION - COMMON REQUIREMENTS

A. Install equipment to allow maximum possible headroom unless specific mounting heights are not indicated.

B. Install equipment level and plumb, parallel and perpendicular to other building systems and components in exposed interior spaces, unless otherwise indicated.

C. Install mechanical equipment to facilitate service, maintenance, and repair or replacement of components.  Connect equipment for ease of disconnecting, with minimum interference to other installations.  Extend grease fittings to accessible locations.

D. Install equipment to allow right of way for piping installed at required slope.

E. Install equipment in accordance with Manufacturer’s recommendations.

3.6 CONCRETE BASES

Coordinate concrete work in this Article with Division 3 Section "Cast-in-Place Concrete" or "Cast-in-Place Concrete (Limited Applications)."

Coordinate below with Division 15 Sections specifying equipment.  Indicate dowel rod quantity, size, and spacing on Drawings.

A. Concrete Bases:  Anchor equipment to concrete base according to equipment manufacturer's written instructions.

1. Construct concrete bases of dimensions indicated, but not less than 4 inches larger in both directions than supported unit.

2. Install dowel rods to connect concrete base to concrete floor.  Unless otherwise indicated, install dowel rods on 18-inch centers around the full perimeter of the base.

3. Install epoxy-coated anchor bolts for supported equipment that extend through concrete base, and anchor into structural concrete floor.

4. Place and secure anchorage devices.  Use supported equipment manufacturer's setting drawings, templates, diagrams, instructions, and directions furnished with items to be embedded.

5. Install anchor bolts to elevations required for proper attachment to supported equipment.

6. Install anchor bolts according to anchor-bolt manufacturer's written instructions.

7. Use 3000-psi, 28-day compressive-strength concrete.

3.7 ERECTION OF METAL SUPPORTS AND ANCHORAGES

A. Cut, fit, and place miscellaneous metal supports accurately in location, alignment, and elevation to support and anchor mechanical materials and equipment or as required.

B. Field Welding:  Comply with AWS D1.1.

3.8 ERECTION OF WOOD SUPPORTS AND ANCHORAGES

A. Cut, fit, and place wood grounds, nailers, blocking, and anchorages to support, and anchor mechanical materials and equipment.

B. Select fastener sizes that will not penetrate members if opposite side will be exposed to view or will receive finish materials.  Tighten connections between members.  Install fasteners without splitting wood members.

C. Attach to substrates as required to support applied loads.

END OF SECTION 230500
BASIC MECHANICAL MATERIALS AND METHODS
230500 - 6

