Electrical Service:

NEC Table 430.250 -   25HP Compressor 208V 3ph requires 59.4 Amps for full load.

NEC Table 430.52  - States that the breaker can be sized at 250% of the full load amps, however it needs to be a thermal/magnetic breaker.  (Squirrel cage — other than Design B energy-efficient  with a Inverse Time Breaker2    Note #2 : 2The values given in the last column also cover the ratings of nonadjustable inverse time types of circuit breakers that may be modified as in 430.52(C)(1), Exception No. 1 and No. 2.

NEC para 430.24 states that the conductors can be sized on