Judge Jim Lamz






02/18/08
Slidell City Court

501 Bouscaren Drive

Slidell, LA  70458

RE:
Slidell City Court Roof Repairs

Dear Judge Lamz,

The following is a transcript of the meeting at your office February 19, 2008.

On Friday December 14th 2007 a leak test was performed on the roof of administration building. The following were present James Bowman, Kirt Dammon, Paul and Art (Mega Air) representing Millennium Roofing, Slidell Fire Dept.
Water stained ceiling tiles were first removed in the small court room and water was applied to the area in which the stained ceiling tiles were located. After approximately ten minutes of applying water to a concentrated area it was determined that the leak was coming from a wire way penetrating the roof on the shingled section. This wire way was plugged with a filler compound but water leaked through the filler. To repair this 90 deg elbow was installed so that the hole looked down not allowing water to enter.
Further testing of the roof revealed a missing flashing on the southwest corner of the small flat roof. Replacement of the flashing and sealing was completed.
Water stains on tile near door to the marshals offices from with in the administration bldg. Next water was applied to the roof which holds the five A/C units concentrating on unit #3. It was determined that in a driving rain water could enter the chassis of the A/C unit and make its way along the exterior of the duct work. To remedy this a flashing was installed to divert any wind driven rain water
The final leak was over the restrooms in the administration bldg. The ventilator on the shingled roof leaks water when there is a wind driven rain. No action was taken at this time.
Mega air completed the repairs to the first three items at no cost. The forth item will be completed as soon as possible. Mega Air has agreed to replace the damaged ceiling tiles at no additional cost the court.
Sincerely,

Kirt Dammon

Dammon Eng.
