DAMMON ENGINEERING, INC.
dammonengineering.com


CONSULTING

DESIGN

STUDIES

EXPERT WITNESS


1095 Florida Ave.



   P.O. Box 2830



     985-649-5832

Slidell, LA 70458



Slidell, LA  70459


            FAX 985-641-5950

July 20, 2007
Judge Jim Lamz

Slidell City Court

501 Bouscaren Drive

Slidell, LA  70458

RE:
Slidell City Court Administration A/C Ducts
Dear Judge Lamz,

Thank you for your letter dated July 19, 2007 we too are anxious to resolve the difficulty in the administration building.
It is our recommendation to replace approximately 25’ of the supply duct insulation on the A/C unit that has been identified, with 3” R-8 insulation.  Also, the existing installation of A/C equipment and duct work does not have inspection doors, which are needed for inspection of the interior of the duct. In this situation, where an old A/C unit is being utilized, we recommend installing an inspection door in the duct. This would allow inspection of the interior of the duct work as it penetrates the roof and the condition of the interior duct work.
After the work is complete and satisfaction is proved, we recommend replacing the supply duct insulation on the remaining A/C units.

The estimated cost to reinsulate one unit is $1,076.00.  To install an inspection door is an additional $200.00 per A/C unit. This work will be done immediately, unless you instruct us otherwise.
Please confirm authorization to proceed.

Sincerely,

Emmett G. (Pete) Dammon, PE

