St. Tammany Parish Administrative Complex

Slidell, Louisiana



SECTION 15410PRIVATE 


PLUMBING PIPING

1 PART 1 GENERAL


1.01

SECTION INCLUDES



A.
Pipe and pipe fittings.



B.
Valves.



C.
Domestic water piping system.



D.
Hot water heating system.



D.
Natural gas piping system.


1.02
seq level2 \h \r0 
REFERENCES



A.
ANSI B31.1 – Power Piping.



B.
ANSI B31.2 – Fuel Gas Piping.



C.
ANSI B31.9 ‑ Building Service Piping.



D.
ASME – Boiler and Pressure Vessel Code.



E.
ASME Sec. 9 – Welding and Brazing Qualifications.



F.
ASME B16.1 – Cast Iron Pipe Flanges and Flanged Fittings Class 25, 125, 250 and 800.



G.  
ASME B16.3 ‑ Malleable Iron Threaded Fittings.



H.
ASME B16.4 ‑ Cast Iron Threaded Fittings Class 125 and 250.



I.
ASME B16.18 ‑ Cast Bronze Solder‑Joint Pressure Fittings.



J.
ASTM A74 – Ferritic Malleable Iron Castings.



K.
ASTM A53 – Pipe, steel, black and hot-dipped zinc coated, welding and seamless.



L.
ASTM A120 – Pipe, steel, black and hot-dipped zinc coated (Galvanized), welded and seamless, for ordinary uses.



M.
ASTM A234 – Pipe Fittings of Wrought Carbon Steel and Alloy Steel for Moderate and Elevated Temperatures.


N.
NCPWB – Procedure Specifications for Pipe Welding.







O.
NFPA 54 – National Fuel Gas Code.

1.03
seq level2 \h \r0 
SUBMITTALS



A.
Submit under provisions of Section 01300.



B.
Product Data: Provide data on pipe materials, pipefittings, valves, and accessories.  Provide manufacturers catalog information.  Indicate valve data and ratings.


1.04
seq level2 \h \r0 
OPERATION AND MAINTENANCE DATA



A.
Submit under provisions of Section 01700.



B.
Maintenance Data:  Include installation instructions, spare parts lists, exploded assembly views.


1.05seq level2 \h \r0 

QUALITY ASSURANCE



A.
Valves: Manufacturer's name and pressure rating marked on valve body.



B.
Welding Materials and Procedures: Conform to ASME Code.



C.
Welders Certification: In accordance with NCPWB Standard Procedure Specifications.



D.
Maintain a copy of each document on site. 

1.06 QUALIFICATIONS

A. Manufacturer:  Company specializing in performing the work of this section with minimum 5 years documented experience.

B. Installer:  Company specializing in performing the work of this section with minimum 5 years documented experience.



seq level2 \h \r0 

1.07
seq level2 \h \r0 
REGULATORY REQUIREMENTS



A.
Perform Work in accordance with State of Louisiana plumbing code.


1.08seq level2 \h \r0 
DELIVERY, STORAGE, AND HANDLING



A.
Accept valves on site in shipping containers with labeling in place.  Inspect for damage.



B.
Provide temporary protective coating on cast iron and steel valves.



C.
Provide temporary end caps and closures on piping and fittings.  Maintain in place until installation.



D.
Protect piping systems from entry of foreign materials by temporary covers, completing sections of the work, and isolating parts of completed system.

PART 2 PRODUCTS

2.02

Provide and install pipe, fittings, and valves to match the existing type, quality and quantity of the existing system.
2.02           GATE VALVES

A. Up to and including 2 Inches (50 mm): Bronze body, bronze trim, non-rising stem, handwheel, inside screw, double wedge or disc, threaded ends.

B. Over 2 inches (50 mm): Iron body, bronze trim, rising stem, handwheel, OS&Y.
2.03         GLOBE VALVES

A. Up to and including 2 Inches (50 mm): Bronze body, bronze trim ,rising stem, handwheel, inside screw, renewable composition disc, screwed ends, with back seating capacity (repackable under pressure)
B. Over 2 Inches (50 mm): Iron body, bronze trim, rising stem, handwheel, OS&Y, plug-type disc, flanged ends, renewable seat and disc.

2.04          BALL VALVES

A. Up to and including 2 Inches (50 mm): Stainless steel one piece body, chrome plated steel ball, Teflon seats and stuffing box ring, lever handle and balancing stops, threaded ends with union.

2.05          PLUG VALVES

A. Up to and including 2 Inches (50 mm):  Bronze body, bronze tapered plug, non-lubricated, Teflon packing, threaded ends.

B. Over 2 Inches (50 mm):  Cast iron body and plug, non-lubricated, Teflon packing, flanged ends.

PART 3 EXECUTION


3.01seq level2 \h \r0 

PREPARATION



A.
Ream pipe and tube ends.
Remove burrs.  



B.
Remove scale and dirt, on inside and outside, before assembly.



C.
Prepare piping connections to equipment with flanges or unions.



D.
Plug all existing pipe systems while system is open for renovation.


3.02
seq level2 \h \r0 
INSTALLATION



A.
Install in accordance with manufacturer's instructions.



B.
Provide non‑conducting dielectric connections wherever jointing dissimilar metals.



C.
Route piping in orderly manner and maintain gradient.



D.
Install piping to conserve building space and not interfere with use of space.



E.
Group piping whenever practical at common elevations.



F.
Install piping to allow for expansion and contraction without stressing pipe, joints, or connected equipment.



G.
Provide clearance for installation of insulation and access to valves and fittings.



H.
Where pipe support members are welded to structural building framing, scrape, brush clean, and apply one coat of zinc rich primer to welding.



I.
Provide support for utility meters in accordance with requirements of utility companies.



J.
Prepare pipe, fittings, supports, and accessories not prefinished, ready for finish painting.  Refer to Section 09900.



K.
Pipe vents from gas pressure reducing valves to outdoors and terminate in weather proof hood.


3.03seq level2 \h \r0 

APPLICATION



A.
Install unions downstream of valves and at equipment or apparatus connections.



B.
Install brass male adapters each side of valves in copper piped system.  Sweat solder adapters to pipe.



C.
Install gate or ball valves for shut‑off and to isolate equipment, part of systems, or vertical risers.

D.
Install ball valves for throttling, bypass, or manual flow control services

E. Provide spring loaded check valves on discharge of water pumps.
F. Provide plug valves in Natural gas systems for shut-off services.

G. Provide flow controls in water recirculating systems where indicated.


3.04
seq level2 \h \r0 
ERECTION TOLERANCES



A.
Establish invert elevations, slopes for drainage to 1/8 inch per foot (2 percent) minimum.  Maintain gradients.



B.
Slope water piping and arrange to drain at low points.

END OF SECTION

PAGE  
PLUMBING PIPING

15410-1

