December 14, 2009

St. Tammany Parish Admin. Complex

520 Old Spanish Trail

Slidell, LA

Re: List of Deficiencies

Note: The following list is a good faith effort for the benefit of all parties, to determine and list completed work that does not conform to contract documents or generally accepted construction industry standards. This list does not include incomplete work. Additional items can be added as they come to light, or removed as they are corrected.

1. Correct landings where they abut main slab.

2. Correct all stair treads to be certain they are equal in width and height.

3. Provide proper fire pump base.

4. Check and repair ceramic tile work where floor is not level and base should be close to 90 degrees.

5. Provide silt fencing in accordance with City permit requirements.

6. Provide construction fencing in accordance with City permit requirements and liability concerns.

7. Verify and provide dimensionally appropriate vehicular flow from Porte Cochere area to and through concrete parking lot already constructed, and concrete parking lot to be constructed.

8. Verify and provide all utilities in “green strip” between parking lot constructed and parking lot to be constructed. Fire Hydrant may need to be relocated.

9. Correct broken flume from parking lot constructed to ditch along Codifer St.

10. Provide compliance with all safety or OSHA requirements throughout project.

11. Provide drinking fountains that do not conflict with Janitor's Closet door at all floors.

12. Correct damage to all installed finishes throughout project.

13. Provide transition ducts as required to accommodate crossovers.

14. Maximum flexible duct length to be 15 feet.

15. Provide gate for raised chiller platform.

16. Seal floor/ceiling penetrations in accordance with requirements of local permitting authorities.

17. Inspect water pipe insulation in place and correct all joints not in compliance with manufacturer's recommendations.

18. Review items to be provided by others, or “By Purchaser”, in elevator shop drawings.

19. Verify compliance with City of Slidell signage requirements.

20. Provide shop drawings never submitted. Coordinate with Architect.

Robert Wiltse

Chief Architect

Dammon Enginering, Inc.

