SLIDELL MEMORIAL HOSPITAL

WOMEN’S IMAGING CENTER

1495 GAUSE BLVD.

Slidell LA  70458

Copyright 2003 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 05500
METAL FABRICATIONS
GLASS UNIT MASONRY ASSEMBLIES This Section uses the term "Architect."  Change this term as necessary to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

Copyright 2002 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 RELATED DOCUMENTS

A. Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 1 Specification Sections, apply to this Section.

1.2 SUMMARY

A. This Section includes the following:

1. Steel framing and supports for operable partitions.

2. Steel framing and supports for mechanical and electrical equipment.

3. Steel framing and supports for applications where framing and supports are not specified in other Sections.

4. Steel girders for supporting wood frame construction.

5. Steel pipe columns for supporting wood frame construction.

Delete first subparagraph below if prefabricated columns are specified in Division 5 Section "Structural Steel."

6. Prefabricated building columns.

Delete subparagraph below if bearing and leveling plates are specified with items that they support.

7. Loose bearing and leveling plates.

Delete subparagraph below if weld plates and angles are specified in same Section as work that is welded to them.

8. Steel weld plates and angles for casting into concrete not specified in other Sections.

Delete first subparagraph below if door frames are attached to steel building frame.

9. Structural-steel door frames.

10. Miscellaneous steel trim.

11. Metal bollards.

12. Pipe guards.

13. Metal downspout boots.

B. Products furnished, but not installed, under this Section include the following:

1. Anchor bolts, steel pipe sleeves, and wedge-type inserts indicated to be cast into concrete or built into unit masonry.

C. Related Sections include the following:

List below only products, construction, and equipment that the reader might expect to find in this Section but are specified elsewhere.

1. Division 3 Section "Cast-in-Place Concrete" for installing anchor bolts, steel pipe sleeves, wedge-type inserts and other items indicated to be cast into concrete.

2. Division 5 Section "Structural Steel."

3. Division 6 Section "Rough Carpentry" for metal framing anchors.

1.3 PERFORMANCE REQUIREMENTS

Paragraph below is for exterior metalwork; revise to suit Project conditions and metalwork exposure.

A. Thermal Movements:  Provide exterior metal fabrications that allow for thermal movements resulting from the following maximum change (range) in ambient and surface temperatures by preventing buckling, opening of joints, overstressing of components, failure of connections, and other detrimental effects.  Base engineering calculation on surface temperatures of materials due to both solar heat gain and nighttime-sky heat loss.

Differential values below (for aluminum in particular) are suitable for most of the U.S.  Revise to suit local conditions.

1. Temperature Change (Range):  120 deg F, ambient; 180 deg F, material surfaces.

1.4 SUBMITTALS

A. Product Data:  For the following:

Delete items below for which Product Data are not required.

1. Nonslip aggregates and nonslip-aggregate surface finishes.

2. Prefabricated building columns.

3. Metal nosings and treads.

4. Paint products.

5. Grout.

B. LEED Submittal:

C. Shop Drawings:  Show fabrication and installation details for metal fabrications.

1. Include plans, elevations, sections, and details of metal fabrications and their connections.  Show anchorage and accessory items.

2. Provide templates for anchors and bolts specified for installation under other Sections.

Retain subparagraph below if products are required to withstand specific design loads and design responsibilities have been delegated to Contractor or if structural data are required as another way to verify products' compliance with performance requirements.  Professional engineer qualifications are specified in Division 1 Section "Quality Requirements."

3. For installed products indicated to comply with design loads, include structural analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

Retain paragraph below if procedures for welder certification are retained in "Quality Assurance" Article.

D. Welding certificates.

1.5 QUALITY ASSURANCE

Delete paragraph below if no welding.  Retain "Welding certificates" Paragraph in "Submittals" Article if retaining below.  AWS states that welding qualifications remain in effect indefinitely unless welding personnel have not welded for more than six months or there is a specific reason to question their ability.

A. Welding:  Qualify procedures and personnel according to the following:

Retain applicable standards below.

1. AWS D1.1, "Structural Welding Code--Steel."

2. AWS D1.2, "Structural Welding Code--Aluminum."

3. AWS D1.3, "Structural Welding Code--Sheet Steel."

4. AWS D1.6, "Structural Welding Code--Stainless Steel."

1.6 PROJECT CONDITIONS

If possible, design metal fabrications so that they do not have to fit other construction, and delete this Article.

A. Field Measurements:  Verify actual locations of walls and other construction contiguous with metal fabrications by field measurements before fabrication and indicate measurements on Shop Drawings.

Delete first subparagraph below if not allowed.

1. Established Dimensions:  Where field measurements cannot be made without delaying the Work, establish dimensions and proceed with fabricating metal fabrications without field measurements.  Coordinate wall and other contiguous construction to ensure that actual dimensions correspond to established dimensions.

2. Provide allowance for trimming and fitting at site.

1.7 COORDINATION

A. Coordinate installation of anchorages for metal fabrications.  Furnish setting drawings, templates, and directions for installing anchorages, including sleeves, concrete inserts, anchor bolts, and items with integral anchors, that are to be embedded in concrete or masonry.  Deliver such items to Project site in time for installation.

Delete paragraph below if not required.

B. Coordinate installation of steel weld plates and angles for casting into concrete that are specified in this Section but required for work of another Section.  Deliver such items to Project site in time for installation.

PART 2 -  PRODUCTS

2.1 MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

Edit this Article with other Part 2 articles in which manufacturers and products are named.  See Division 1 Section "Product Requirements" for an explanation of the terms "Available Products," "Products," "Available Manufacturers," and "Manufacturers" and the effect these terms have on "Comparable Product" and "Product Substitution" requirements.

A. In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

1. Available Products:  Subject to compliance with requirements, products that may be incorporated into the Work include, but are not limited to, products specified.

2. Products:  Subject to compliance with requirements, provide one of the products specified.

3. Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.

4. Manufacturers:  Subject to compliance with requirements, provide products by one of the manufacturers specified.

2.2 METALS, GENERAL

A. Metal Surfaces, General:  Provide materials with smooth, flat surfaces, unless otherwise indicated.  For metal fabrications exposed to view in the completed Work, provide materials without seam marks, roller marks, rolled trade names, or blemishes.

2.3 FERROUS METALS

Retain material types, qualities, and grades in this Article that are indicated in Specifications or on Drawings for each fabrication type.  Add or delete items to suit Project.

A. Steel Plates, Shapes, and Bars:  ASTM A 36/A 36M.

B. Stainless-Steel Sheet, Strip, Plate, and Flat Bars:  ASTM A 666, Type 304.

Usually select Type 304 in paragraph above and below; select Type 316L if required for corrosive environments.

C. Stainless-Steel Bars and Shapes:  ASTM A 276, Type 304.

First paragraph below specifies minimum yield point of 30 ksi (205 MPa); revise if higher strength is required.

D. Rolled-Steel Floor Plate:  ASTM A 786/A 786M, rolled from plate complying with ASTM A 36/A 36M or ASTM A 283/A 283M, Grade C or D.

E. Rolled-Stainless-Steel Floor Plate:  ASTM A 793.

Products in list below have abrasive material metallically bonded to steel by a proprietary process.

F. Steel Tubing:  ASTM A 500, cold-formed steel tubing.

Round steel tubing and pipe are sized differently.  Tubing is designated by OD and wall thickness.  Pipe is designated by nominal pipe size and weight or schedule number.  See Evaluations.

G. Steel Pipe:  ASTM A 53/A 53M, standard weight (Schedule 40), unless another weight is indicated or required by structural loads.

Paragraph below describes typical component of metal channel framing systems such as that manufactured by Unistrut Corporation.

H. Slotted Channel Framing:  Cold-formed metal channels with continuous slot complying with MFMA-3.

Revise paragraph below after verifying availability if another class is required for structural reasons.  Insert ductile iron if needed for structural reasons.

I. Cast Iron:  ASTM A 48/A 48M, Class 30, unless another class is indicated or required by structural loads.

2.4 NONFERROUS METALS

Retain material types, qualities, and grades in this Article that are indicated in Specifications or on Drawings for each fabrication type.  Add or delete items to suit Project.

A. Aluminum Plate and Sheet:  ASTM B 209, Alloy 6061-T6.

B. Aluminum Extrusions:  ASTM B 221, Alloy 6063-T6.

C. Aluminum-Alloy Rolled Tread Plate:  ASTM B 632/B 632M, Alloy 6061-T6.

D. Aluminum Castings:  ASTM B 26/B 26M, Alloy 443.0-F.

E. Bronze Plate, Sheet, Strip, and Bars:  ASTM B 36/B 36M, Alloy UNS No. C28000 (muntz metal, 60 percent copper).

F. Bronze Extrusions:  ASTM B 455, Alloy UNS No. C38500 (extruded architectural bronze).

G. Bronze Castings:  ASTM B 584, Alloy UNS No. C83600 (leaded red brass) or No. C84400 (leaded semired brass).

H. Nickel Silver Extrusions:  ASTM B 151/B 151M, Alloy UNS No. C74500.

I. Nickel Silver Castings:  ASTM B 584, Alloy UNS No. C97600 (20 percent leaded nickel bronze).

2.5 FASTENERS

Usually select Type 304 in paragraph below; select Type 316 if required for corrosive environments.

A. General:  Unless otherwise indicated, provide Type 304 stainless-steel fasteners for exterior use and zinc-plated fasteners with coating complying with ASTM B 633, Class Fe/Zn 5, at exterior walls.  Provide stainless-steel fasteners for fastening aluminum.  Select fasteners for type, grade, and class required.

Delete remainder of this Article unless there are specific requirements for these types of fasteners.  Revise paragraph below if ASTM A 325 bolts are required for connecting miscellaneous steel framing and supports.

B. Steel Bolts and Nuts:  Regular hexagon-head bolts, ASTM A 307, Grade A; with hex nuts, and, where indicated, flat washers.

C. Anchor Bolts:  ASTM F 1554, Grade 36.

1. Provide hot-dip or mechanically deposited, zinc-coated anchor bolts where item being fastened is indicated to be galvanized.

D. Eyebolts:  ASTM A 489.

E. Machine Screws:  ASME B18.6.3.

F. Lag Bolts:  ASME B18.2.1.

G. Wood Screws:  Flat head, ASME B18.6.1.

H. Plain Washers:  Round, ASME B18.22.1.

I. Lock Washers:  Helical, spring type, ASME B18.21.1.

Delete first paragraph and subparagraph below if not applicable.  If retaining, verify safety factor with Project's structural engineer.

J. Cast-in-Place Anchors in Concrete:  Anchors capable of sustaining, without failure, a load equal to four times the load imposed, as determined by testing according to ASTM E 488, conducted by a qualified independent testing agency.

1. Threaded or wedge type; galvanized ferrous castings, either ASTM A 47/A 47M malleable iron or ASTM A 27/A 27M cast steel.  Provide bolts, washers, and shims as needed, hot-dip galvanized per ASTM A 153/A 153M.

K. Expansion Anchors:  Anchor bolt and sleeve assembly with capability to sustain, without failure, a load equal to six times the load imposed when installed in unit masonry and four times the load imposed when installed in concrete, as determined by testing according to ASTM E 488, conducted by a qualified independent testing agency.

1. Material for Anchors in Interior Locations:  Carbon-steel components zinc-plated to comply with ASTM B 633, Class Fe/Zn 5.

Subparagraph above and below are examples only.  Material above protects against corrosion in an indoor atmosphere; revise to suit other conditions after verifying availability of thicker coatings.  In subparagraph below, Alloy Group 1 (A1) refers to Type 304 and similar alloys, and Alloy Group 2 (A4) refers to Type 316 and similar alloys.

2. Material for Anchors in Exterior Locations:  Alloy Group 1 stainless-steel bolts complying with ASTM F 593 and nuts complying with ASTM F 594.

2.6 MISCELLANEOUS MATERIALS

A. Welding Rods and Bare Electrodes:  Select according to AWS specifications for metal alloy welded.

B. Shop Primers:  Provide primers that comply with Division 9 Painting Sections.

Select paragraph above or one or both primer paragraphs and associated subparagraphs below.  First paragraph below specifies a typical primer for painted finishes that provides minimum protection to steel.  Second paragraph specifies a typical primer for high-performance coating.  If retaining both, indicate on Drawings or in a schedule where each is required.

C. Universal Shop Primer:  Fast-curing, lead- and chromate-free, universal modified-alkyd primer complying with MPI#79.

Delete subparagraph below if zinc-rich primer is not used.

1. Use primer containing pigments that make it easily distinguishable from zinc-rich primer.

D. Zinc-Rich Primer:  Complying with SSPC-Paint 20 or SSPC-Paint 29 and compatible with topcoat.

Coordinate subparagraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.  Edit list to suit local VOC regulations.

1. Available Products:

a. Benjamin Moore & Co.; Epoxy Zinc-Rich Primer CM18/19.

b. Carboline Company; Carbozinc 621.

c. ICI Devoe Coatings; Catha-Coat 313.

d. International Coatings Limited; Interzinc 315 Epoxy Zinc-Rich Primer.

e. PPG Architectural Finishes, Inc.; Aquapon Zinc-Rich Primer 97-670.

f. Sherwin-Williams Company (The); Corothane I GalvaPac Zinc Primer.

g. Tnemec Company, Inc.; Tneme-Zinc 90-97.

Delete first paragraph below if no galvanized fabrications.

E. Galvanizing Repair Paint:  High-zinc-dust-content paint for regalvanizing welds in steel, complying with SSPC-Paint 20.

F. Bituminous Paint:  Cold-applied asphalt emulsion complying with ASTM D 1187.

Retain paragraph below for heavy-duty grouting applications.  Do not use in wet areas or on exterior.

G. Nonshrink, Metallic Grout:  Factory-packaged, ferrous-aggregate grout complying with ASTM C 1107, specifically recommended by manufacturer for heavy-duty loading applications.

Retain paragraph below for grouting applications where nonstaining grout is required.

H. Nonshrink, Nonmetallic Grout:  Factory-packaged, nonstaining, noncorrosive, nongaseous grout complying with ASTM C 1107.  Provide grout specifically recommended by manufacturer for interior and exterior applications.

Delete paragraph below if not required for concrete-filled bollards, footings for bollards, or wheel guards.

I. Concrete Materials and Properties:  Comply with requirements in Division 3 Section "Cast-in-Place Concrete" for normal-weight, air-entrained, ready-mix concrete with a minimum 28-day compressive strength of 3000 psi, unless otherwise indicated.

2.7 FABRICATION, GENERAL

A. Shop Assembly:  Preassemble items in the shop to greatest extent possible.  Disassemble units only as necessary for shipping and handling limitations.  Use connections that maintain structural value of joined pieces.  Clearly mark units for reassembly and coordinated installation.

B. Cut, drill, and punch metals cleanly and accurately.  Remove burrs and ease edges to a radius of approximately 1/32 inch, unless otherwise indicated.  Remove sharp or rough areas on exposed surfaces.

C. Form bent-metal corners to smallest radius possible without causing grain separation or otherwise impairing work.

D. Form exposed work true to line and level with accurate angles and surfaces and straight edges.

E. Weld corners and seams continuously to comply with the following:

1. Use materials and methods that minimize distortion and develop strength and corrosion resistance of base metals.

2. Obtain fusion without undercut or overlap.

3. Remove welding flux immediately.

4. At exposed connections, finish exposed welds and surfaces smooth and blended so no roughness shows after finishing and contour of welded surface matches that of adjacent surface.

F. Form exposed connections with hairline joints, flush and smooth, using concealed fasteners where possible.  Where exposed fasteners are required, use Phillips flat-head (countersunk) screws or bolts, unless otherwise indicated.  Locate joints where least conspicuous.

G. Fabricate seams and other connections that will be exposed to weather in a manner to exclude water.  Provide weep holes where water may accumulate.

H. Cut, reinforce, drill, and tap metal fabrications as indicated to receive finish hardware, screws, and similar items.

I. Provide for anchorage of type indicated; coordinate with supporting structure.  Space anchoring devices to secure metal fabrications rigidly in place and to support indicated loads.

1. Where units are indicated to be cast into concrete or built into masonry, equip with integrally welded steel strap anchors, 1/8 by 1-1/2 inches, with a minimum 6-inch  embedment and 2-inch hook, not less than 8 inches from ends and corners of units and 24 inches o.c., unless otherwise indicated.

First 17 articles below specify fabrication requirements for typical metal fabrications; delete those not required, edit those retained to suit Project, and add others as required.

2.8 MISCELLANEOUS FRAMING AND SUPPORTS

A. General:  Provide steel framing and supports not specified in other Sections as needed to complete the Work.

B. Fabricate units from steel shapes, plates, and bars of welded construction, unless otherwise indicated.  Fabricate to sizes, shapes, and profiles indicated and as necessary to receive adjacent construction retained by framing and supports.  Cut, drill, and tap units to receive hardware, hangers, and similar items.

Delete two subparagraphs below if not required.

1. Fabricate units from slotted channel framing where indicated.

2. Furnish inserts if units are installed after concrete is placed.

Requirements below are examples only; revise to suit Project.  Add similar provisions for other supports, such as for ceiling-hung toilet compartments, overhead doors, etc.  Base support and bracing sizes on recommendations of manufacturer of item being supported.  Insert requirements for other specific applications.

C. Fabricate supports for operable partitions from continuous steel beams of sizes indicated with attached bearing plates, anchors, and braces as indicated.  Drill bottom flanges of beams to receive partition track hanger rods; locate holes where indicated on operable partition Shop Drawings.

Revise paragraph and subparagraphs below if girders are spliced.  Add ASTM A 325 bolts to "Fasteners" Article if required for splicing or for connecting to pipe columns.

D. Fabricate steel girders for wood frame construction from continuous steel shapes of sizes indicated.

1. Provide bearing plates welded to beams where indicated.

2. Drill girders and plates for field-bolted connections where indicated.

Delete subparagraph below if nailers are not used or are fastened with powder-actuated fasteners.

3. Where wood nailers are attached to girders with bolts or lag screws, drill holes at 24 inches o.c.

Revise first paragraph and subparagraphs below if tubing is used.  Revise default weld size requirement, or delete and detail welds on Drawings to suit Project.

E. Fabricate steel pipe columns for supporting wood frame construction from steel pipe with steel baseplates and top plates as indicated.  Drill baseplates and top plates for anchor and connection bolts and weld to pipe with fillet welds all around.  Make welds the same size as pipe wall thickness, unless otherwise indicated.

1. Unless otherwise indicated, fabricate from Schedule 40 steel pipe.

2. Unless otherwise indicated, provide 1/2-inch baseplates with four 5/8-inch anchor bolts and 1/4-inch top plates.

F. Galvanize miscellaneous framing and supports where indicated.

Select paragraph above or below if required.  If retaining either, indicate galvanized or zinc-rich primed items on Drawings.

G. Prime miscellaneous framing and supports with zinc-rich primer where indicated.

2.9 PREFABRICATED BUILDING COLUMNS

Delete this Article if prefabricated building columns are specified in Division 5 Section "Structural Steel."

A. General:  Provide prefabricated building columns consisting of load-bearing structural-steel members protected by insulating concrete fireproofing encased in an outer non-load-bearing steel shell.

B. Column Configuration:  Provide columns of sizes and shapes indicated.  Fabricate connections to comply with details shown or as needed to suit type of structure indicated.

1. Concrete Fill:  Manufacturer's standard structural concrete, with minimum compressive strength of 4200 psi, machine mixed and mechanically vibrated during placement to produce concrete core free of voids.

Coordinate paragraph and list below with Part 2 "Manufacturers" Article.  Retain "Available" for nonproprietary and delete for semiproprietary specifications.

C. Available Manufacturers:

1. Black Rock Column, Inc.

2. Dean, George H., Inc.

3. Firetrol Division; Dean Lally L. P.

2.10 LOOSE BEARING AND LEVELING PLATES

A. Provide loose bearing and leveling plates for steel items bearing on masonry or concrete construction.  Drill plates to receive anchor bolts and for grouting.

B. Galvanize plates after fabrication.

Select paragraph above or below if required.

C. Prime plates with zinc-rich primer.

2.11 STEEL WELD PLATES AND ANGLES

A. Provide steel weld plates and angles not specified in other Sections, for items supported from concrete construction as needed to complete the Work.  Provide each unit with not less than two integrally welded steel strap anchors for embedding in concrete.

2.12 STRUCTURAL-STEEL DOOR FRAMES

Retain this Article for structural-steel door frames built into masonry or concrete walls and not attached to structural-steel building frame.  Door frames connected to structural-steel framing are specified with that work in another Division 5 Section.

A. Fabricate structural-steel door frames from steel shapes, plates, and bars of size and to dimensions indicated, fully welded together, with 5/8-by-1-1/2-inch steel channel stops, unless otherwise indicated.  Plug-weld built-up members and continuously weld exposed joints.  Secure removable stops to frame with countersunk machine screws, uniformly spaced at not more than 10 inches o.c.  Reinforce frames and drill and tap as necessary to accept finish hardware.

1. Provide with integrally welded steel strap anchors for securing door frames into adjoining concrete or masonry.

Delete first paragraph below if not required.

B. Extend bottom of frames to floor elevation indicated with steel angle clips welded to frames for anchoring frame to floor with expansion shields and bolts.

C. Galvanize exterior steel frames.

Select paragraph above or below if required.  If retaining "interior steel frames" option in either, indicate galvanized or zinc-rich primed items on Drawings.

D. Prime interior steel frames with zinc-rich primer.

2.13 MISCELLANEOUS STEEL TRIM

A. Unless otherwise indicated, fabricate units from steel shapes, plates, and bars of profiles shown with continuously welded joints and smooth exposed edges.  Miter corners and use concealed field splices where possible.

B. Provide cutouts, fittings, and anchorages as needed to coordinate assembly and installation with other work.

1. Provide with integrally welded steel strap anchors for embedding in concrete or masonry construction.

C. Galvanize exterior miscellaneous steel trim.

Select paragraph above or below if required.  If retaining "interior miscellaneous steel trim" option in either, indicate galvanized or zinc-rich primed items on Drawings.

D. Prime interior miscellaneous steel trim with zinc-rich primer.

2.14 METAL BOLLARDS

Usually select Schedule 40 steel pipe in paragraph below.  Schedule 80 is suitable for security applications.

A. Fabricate metal bollards from Schedule 40 steel pipe.

2.15 PIPE GUARDS

Paragraph below is an example of pipe protection for parking garages and other locations where pipes are subject to damage by vehicles.

A. Fabricate pipe guards from 3/8-inch thick by 12-inch wide steel plate, bent to fit flat against the wall or column at both ends and to fit around pipe with 2-inch clearance between pipe and pipe guard.  Drill each end for two 3/4-inch anchor bolts.

Delete paragraph below if not required.

B. Galvanize pipe guards after fabrication.

2.16 METAL DOWNSPOUT BOOTS

A. Provide downspout boots made from in heights indicated with inlets of size and shape to suit downspouts.

2.17 FINISHES, GENERAL

A. Comply with NAAMM's "Metal Finishes Manual for Architectural and Metal Products" for recommendations for applying and designating finishes.

B. Finish metal fabrications after assembly.

2.18 STEEL AND IRON FINISHES

A. Galvanizing:  Hot-dip galvanize items as indicated to comply with applicable standard listed below:

1. ASTM A 123/A 123M, for galvanizing steel and iron products.

2. ASTM A 153/A 153M, for galvanizing steel and iron hardware.

B. Preparation for Shop Priming:  Prepare uncoated ferrous-metal surfaces to comply with minimum requirements indicated below for SSPC surface preparation specifications and environmental exposure conditions of installed metal fabrications:

Retain or revise both subparagraphs below to suit Project service conditions of installed work.  Insert other exposures and preparation requirements where applicable.  Refer to SSPC's painting manual.  Both subparagraphs apply to locations that would normally remain dry in service.

1. Exteriors (SSPC Zone 1B) and Items Indicated to Receive Zinc-Rich Primer:  SSPC-SP 6/NACE No. 3, "Commercial Blast Cleaning."

2. Interiors (SSPC Zone 1A):  SSPC-SP 3, "Power Tool Cleaning."

C. Shop Priming:  Apply shop primer to uncoated surfaces of metal fabrications, except those with galvanized finishes and those to be embedded in concrete, sprayed-on fireproofing, or masonry, unless otherwise indicated.  Comply with SSPC-PA 1, "Paint Application Specification No. 1: Shop, Field, and Maintenance Painting of Steel," for shop painting.

Delete subparagraph below if not required.  Stripe painting adds cost but helps ensure that hard-to-reach areas, such as crevices, inside corners, and welds, are thoroughly coated and that sharp edges (which are vulnerable to chipping and are where the film may be thinner due to surface tension) receive adequate coverage.

1. Stripe paint corners, crevices, bolts, welds, and sharp edges.

2.19 STAINLESS-STEEL FINISHES

Delete this Article if no stainless steel.

A. Remove tool and die marks and stretch lines or blend into finish.

Delete paragraph below if no directionally textured finishes are retained.

B. Grind and polish surfaces to produce uniform, directionally textured, polished finish indicated, free of cross scratches.  Run grain with long dimension of each piece.

First two paragraphs below specify typical stainless-steel finishes and reference standard sheet finish designations.  Revise if another finish is required.

C. Bright, Directional Satin Finish:  No. 4.

D. Dull Satin Finish:  No. 6.

E. When polishing is completed, passivate and rinse surfaces.  Remove embedded foreign matter and leave surfaces chemically clean.

2.20 ALUMINUM FINISHES

Delete this Article if no aluminum.

A. Finish designations prefixed by AA comply with the system established by the Aluminum Association for designating aluminum finishes.

Retain finishes in two paragraphs below to suit Project.  If retaining more than one, indicate location of each on Drawings or by inserts.

B. As-Fabricated Finish:  AA-M10 (Mechanical Finish:  as fabricated, unspecified).

Finish in paragraph above is usually referred to as "mill finish." Finish below is heavy-anodized finish; before specifying, verify availability with manufacturers selected.

C. Class I, Clear Anodic Finish:  AA-M12C22A41 (Mechanical Finish:  nonspecular as fabricated; Chemical Finish:  etched, medium matte;  Anodic Coating:  Architectural Class I, clear coating 0.018 mm or thicker) complying with AAMA 611.

PART 3 -  EXECUTION

3.1 INSTALLATION, GENERAL

A. Cutting, Fitting, and Placement:  Perform cutting, drilling, and fitting required for installing metal fabrications.  Set metal fabrications accurately in location, alignment, and elevation; with edges and surfaces level, plumb, true, and free of rack; and measured from established lines and levels.

B. Fit exposed connections accurately together to form hairline joints.  Weld connections that are not to be left as exposed joints but cannot be shop welded because of shipping size limitations.  Do not weld, cut, or abrade surfaces of exterior units that have been hot-dip galvanized after fabrication and are for bolted or screwed field connections.

C. Field Welding:  Comply with the following requirements:

1. Use materials and methods that minimize distortion and develop strength and corrosion resistance of base metals.

2. Obtain fusion without undercut or overlap.

3. Remove welding flux immediately.

4. At exposed connections, finish exposed welds and surfaces smooth and blended so no roughness shows after finishing and contour of welded surface matches that of adjacent surface.

D. Fastening to In-Place Construction:  Provide anchorage devices and fasteners where metal fabrications are required to be fastened to in-place construction.  Provide threaded fasteners for use with concrete and masonry inserts, toggle bolts, through bolts, lag bolts, wood screws, and other connectors.

E. Provide temporary bracing or anchors in formwork for items that are to be built into concrete, masonry, or similar construction.

Delete paragraph below if no aluminum.

F. Corrosion Protection:  Coat concealed surfaces of aluminum that will come into contact with grout, concrete, masonry, wood, or dissimilar metals with a heavy coat of bituminous paint.

Delete articles below not applicable to Project.  Insert others where needed to specify requirements applicable to a specific item not covered under general installation requirements above.

3.2 INSTALLING MISCELLANEOUS FRAMING AND SUPPORTS

A. General:  Install framing and supports to comply with requirements of items being supported, including manufacturers' written instructions and requirements indicated on Shop Drawings.

B. Anchor supports for operable partitions securely to and rigidly brace from building structure.

C. Support steel girders on solid grouted masonry, concrete, or steel pipe columns.  Secure girders with anchor bolts embedded in grouted masonry or concrete or with bolts through top plates of pipe columns.

Delete subparagraph below if not required.

1. Where grout space under bearing plates is indicated for girders supported on concrete or masonry, install as specified in "Installing Bearing and Leveling Plates" Article.

D. Install pipe columns on concrete footings with grouted baseplates.  Position and grout column baseplates as specified in "Installing Bearing and Leveling Plates" Article.

Delete subparagraph below if no pipe columns supporting steel girders.

1. Grout baseplates of columns supporting steel girders after girders are installed and leveled.

3.3 INSTALLING PREFABRICATED BUILDING COLUMNS

Delete this Article if prefabricated building columns are specified in Division 5 Section "Structural Steel."

A. Install prefabricated building columns to comply with AISC's "Specification for Structural Steel Buildings Allowable Stress Design and Plastic Design with Commentary" and with requirements applicable to listing and labeling for fire-resistance rating indicated.

3.4 INSTALLING BEARING AND LEVELING PLATES

A. Clean concrete and masonry bearing surfaces of bond-reducing materials, and roughen to improve bond to surfaces.  Clean bottom surface of plates.

B. Set bearing and leveling plates on wedges, shims, or leveling nuts.  After bearing members have been positioned and plumbed, tighten anchor bolts.  Do not remove wedges or shims but, if protruding, cut off flush with edge of bearing plate before packing with grout.

Revise subparagraph below if only metallic grout is used at concealed, protected locations.

1. Use nonshrink grout, either metallic or nonmetallic, in concealed locations where not exposed to moisture; use nonshrink, nonmetallic grout in exposed locations, unless otherwise indicated.

Delete subparagraph below if not required.

2. Pack grout solidly between bearing surfaces and plates to ensure that no voids remain.

3.5 INSTALLING NOSINGS, TREADS, AND THRESHOLDS

A. Seal thresholds exposed to exterior with elastomeric sealant complying with Division 7 Section "Joint Sealants" to provide a watertight installation.

3.6 ADJUSTING AND CLEANING

A. Touchup Painting:  Immediately after erection, clean field welds, bolted connections, and abraded areas.  Paint uncoated and abraded areas with the same material as used for shop painting to comply with SSPC-PA 1 for touching up shop-painted surfaces.

1. Apply by brush or spray to provide a minimum 2.0-mil dry film thickness.

Retain paragraph and subparagraph above if touchup painting is included in this Section.  Retain first paragraph below if it is specified in Division 9 painting Sections.  Revise reference if another Division 9 Section, such as "High-Performance Coatings," is used.

B. Touchup Painting:  Cleaning and touchup painting of field welds, bolted connections, and abraded areas of shop paint are specified in Division 9 painting Sections.

C. Galvanized Surfaces:  Clean field welds, bolted connections, and abraded areas and repair galvanizing to comply with ASTM A 780.

END OF SECTION
METAL FABRICATIONS

05500 - 13

