Riverine and Combatant Craft Operation Facility

Stennis Space Center, MS

URS 50% Design Submittal Comments 

with Broadmoor Responses and 

Additional URS Commentary in Blue

(i.e. only those with blue require additional action)

17 November 2009

Designer Response (17 November 2009) in Green

Architectural Drawings

Comments

General
Provide a sheet indicating symbols, abbreviations, and their meaning (sheet cut on, sheet shown on, etc.).  Locations of section cuts shown in this drawing set are difficult to trace.

Corrected by designer.

General
Provide a Life Safety Plan for each building indicating fire separations, access to exits, exit capacity, occupancies of each space, travel distances to exits, etc.

Life Safety Plan to be provided by DBFPE and coordinated with Architect.

SEE SHEETS LS.1 AND LS.2.

General
Why is 5/12 roof slope proposed on Buildings 2440 and 2442 and 4/12 slope proposed on Building 2441?

As discussed at recent review meeting, to avoid undesirable roof plan.

Cover 1 and 2
Delete “NASA” from title of the project.

Corrected by designer.

**Cover 2
Obtain written concurrence of NAVFAC Fire Protection Engineer that the Maintenance and Staging Building (2441) is F-1 occupancy instead of H occupancy.  

Will be coordinated by Architect.

DBFPE IS COORDINATING WITH THE NAVFAC FPE TO PROVIDE DOCUMENTATION.

See attached letter from Matthew Morse on revised CD.

Where is the letter referred to in the latest response? If it is the same letter involving fire protection comments, we do not think it explicitly addresses this issue.

Matthew Morse has rejected F-1 occupancy and is requiring S-1.

**Cover 2
None of the square footages for space or floor match the square footages indicated on the drawings (A1.1 or A1.2). As an example:  1st Floor – 8,759 SF vs. 8,584 SF; 
Cages – 4,467 SF vs. 4,516 SF; Armory – 1,456 SF vs. 1,484 SF; and Maint/Staging area – 6,642 SF vs. 6,879 SF.  The number of occupants may need to be re-stated once you determine which statements of area are correct.  

Corrected by designer.

Has been corrected.

Square footage discrepancy on T-3, LS.1 and A1.1 has not been corrected, BUT, if you change the 1st floor SF for Building 2440 on T-3 and LS.1 to 8,691 SF, this will fix the problem.

Square footage corrected to 6,879 for all drawings.

Cover 2
Under “Exit Access Requirements,” the correct reference should be to Table 1015.1 (not to Section 1014), and the correct wording should be that “2 exits are required for greater than 49 occupants.”

Will be corrected by designer and Architect.

SEE SHEETS T-3, LS.1 AND LS.2.

**Cover 2
For exits from the Armory, refer to 1015.2.1, Exception 1, which says that for buildings equipped with an automatic sprinkler system in accordance with Section 903.3.1.1 or 903.3.1.2, the separation distance of the exit doors shall be not less than 1/3 of the length of the maximum overall diagonal dimension of the area served.  You may need to add an exit or move one of the exits further from the other.

Will be reviewed and coordinated with DBFPE. Occupant load of 15 may require only one exit.

DBFPE HAS DETERMINED ONLY ONE EXIT IS REQUIRED.

Repeat:  DBFPE s not the Authority Having Jurisdiction (AHJ).  What is the AHJ’s response to this issue?

Referred to DBFPE / AHJ.

Cover 2
Exit access travel distance per Table 1016.1 is 250 feet for F-1, occupancy with a sprinkler system, not 300 feet as indicated on this drawing.

Corrected by designer.

Cover 2
Delete Exit access travel distance for H-1 occupancy if there is no H-1 occupancy area.

Corrected by designer.

**Cover 2
Allowable Height and Building Area has conflicts.  First floor of Building 2440 is not 6,554 SF on the 1st floor, nor 6,682 SF on the 2nd floor (per Sheet A1.1).  Similarly, Building 2441 stated area of 8,098 SF does not agree with Sheet A1.1.  Please revise after you have rectified the actual square footages.

Areas to be corrected by designer and will be reviewed by Architect.

REVISED FIGURES INDICATED ON LS.1, LS.2, A1.1, A1.2, AND A2.1.

Has been corrected.

Square footage discrepancy on T-3, LS.1 and A1.1 has not been corrected, BUT, if you change the 1st floor SF for Building 2440 on T-3 and LS.1 to 8,691 SF, this will fix the problem.

Square footage corrected to 6,879 for all drawings.

Cover 2
Despite the fact that the Facility (Stennis or NAVFAC) has designated 2440 and 2441 as two buildings, are they not - for construction and code purposes – one building with ‘mixed use (non-separated) occupancy?   If so, how does this affect the code analysis?  If they are two separate buildings, it appears that they could require a fire-resistant wall between them per Table 602 (X<5 feet).

Will be reviewed and coordinated with DBFPE. Architect intends to detail a rated wall between 2440 & 2441.

RATED CONSTRUCTION HAS BEEN DETAILED IN THE PLANS.

Cover 2
Verify that a fire protection system is required by 903.2.3 as stated in your code analysis.  

Will be reviewed by Architect.

A FIRE PROTECTION SYSTEM IS NOT REQUIRED BY 903.2.3 BECAUSE THE F-1 AREA IS UNDER THE SQUARE FOOTAGE REQUIREMENT.

Cover 2
Verify Basic Wind Speed of 130 MPH, since this indicates it came from Figure 1609 (IBC) alone, not from IBC, ASCE 7-02, and UFC 3-310-01, as required by RFP Part 4, Section B10 1.3.2.2.

UFC 3-310-01 calls for Wind Speed of 130 MPH at Stennis. Engineering staff to review.

ENGINEERING REVIEW VERIFIES ABOVE 130 MPH REQUIREMENT FROM UFC3-310-01.

The word “above” has been removed.  UFC 3-310-01 required 130 mph.

Cover 2
Use Importance Factor of II per RFP Part 4, Section B10 1.3.2.1, not III as indicated on this drawing.  Recalculate all design loads listed based on the correct parameters.

Will be reviewed by engineering staff.

ALL CURRENT CALCULATIONS ARE BASED ON AN IMPORTANCE FACTOR OF II.

Cover 2
Life Safety Code Analysis – Add Building 2442 to this analysis.

Will be reviewed and coordinated with DBFPE and added to package.

SEE SHEET LS.2.

Cover 2
Life Safety Code Analysis – Per NFPA 101, Table 6.1.14.4.4(b), Business Occupancies are required to be separated from all Industrial and Storage occupancies by 2-hour rated construction (and may be reduced to 1-hour with an approved automatic sprinkler system).

Will be reviewed and coordinated with DBFPE.

ONE HOUR RATED SEPARATION IS DETAILED ON PLANS FOR THIS AREA.

Has been corrected.

Cover 2
Life Safety Code Analysis – Check square footages, they need to match what is on the plan sheets.

Will be reviewed and coordinated with DBFPE.

SQUARE FOOTAGES REVIEWED.

Cover 2
Life Safety Code Analysis – Verify whether or not the Armory is a High Hazard Occupancy, and modify your analysis accordingly.

Will be reviewed and coordinated with DBFPE.

ARMORY REVISED TO MODERATE HAZARD, ANALYSIS MODIFIED.

**Cover 2
Life Safety Code Analysis – Use of 100 SF/ person and 45 occupants for cages conflicts with Building Code analysis.  Please be consistent.

Will be reviewed and coordinated with DBFPE.

CAGE ANALYSIS REVISED, SEE T-3 AND LS.1.

Has been corrected.

Repeat:  We feel that 10 persons in the cage area is unrealistically low.  Please confirm this number with the users and adjust accordingly.

Referred to DBFPE.

Cover 2
Life Safety Code Analysis – Exit Access Travel Distance for sprinklered General Industrial Occupancies is 250 feet per Table A.7.6., not 300 feet as indicated on this drawing.

Corrected by designer.

Cover 2 
In the Building Code Analysis for Building 2441, does the square footage on this sheet match the square footage of this building as indicated on Sheet A2.1?

Corrected by designer.

Cover 2
Revise Basic Wind Speed, Importance Factor, and all load analysis for Building 2442 in accordance with previous comments for Buildings 2440 and 2441.

Will be reviewed by engineering staff.

CURRENT CALCULATIONS REVISED.

General
Ensure that formal interviews with the Users are performed and that the results are well documented and distributed to all relevant parties.  

Interview conducted on 12/17/08, will verify documentation and distribution.

DOCUMENTATION AND DISTRIBUTION HAS BEEN CONDUCTED.

S1.1
Show cage pedestals on this drawing.  (Repeat Comment from Concept Submittal).

Corrected by designer.

Shown on S1.2

S1.1
Make sure to accommodate drains in cage area, heads, showers, mechanical room, as well as trench drains in boat maintenance area.  (Repeat Comment from Concept Submittal).

Will be corrected by designer and coordinated with Mechanical Engineer.

DRAINS ARE SHOWN AND DETAILED ON CURRENT ARCHITECTURAL, STRUCTURAL, AND MECHANICAL PLANS.

Shown on S1.2

A1.1
Door from Cages 105 to Stairs 115 should swing in the direction of egress (from Cages to Stairs), not as currently shown.

Corrected by designer.

Correct on Final Set.

**A1.1
Per previous comment, relocate doors to comply with separation requirement.

Corrected by designer.

Comment was for this, not comment No. 27, for which response was given.  Comment deals with location of doors in the Armory.

Referred to DBFPE.

A1.1
Indicate extent of roof overhangs on this drawing.

Corrected by designer.

A1.1
Should bollards be provided on the inside of the Maintenance and Staging area to protect coiling doors from the inside?

Discussed at recent review meeting, deleted by User.

A1.1
Provide indication of where exterior elevations are cut/shown.

Corrected by designer.

A1.1
Please explain need for Vault Door Hinge on Door 01.

Corrected and deleted by designer.

A1.1
Provide elevations of doors and frames to accompany door schedule.

Will be provided by designer and Architect.

Elevation of vault door has been added.

SEE SHEET A1.18.

A1.1
If Door 02 is going to function as an entrance door, it should have an entrance mat, be an insulated door, have min 6” x 12” vision panels (1 per leaf), and have a knox box.

Corrected by designer.

A1.1
Indicate Door 03 at Side Entry 104 and Rear Entry 101 are to be hollow metal, have an entrance mat, knox box, and min 6” x 12” vision panel – or make this a different door number.  Door 03 shown at other locations should be indicated as hollow metal.

Corrected by designer.

Has been corrected.

A1.1
Please explain the requirement for a deadbolt on Door 04(s).

Corrected and deleted by designer.

A1.1
Please explain requirement for STC of 42 for Door(s) 09.

Corrected and deleted by designer.

Door marked 9 then, is now marked 25 with no STC requirement.

A1.1
Indicate materials and hardware requirements for Door 05 and Door 017. 

Corrected by designer.

A1.1
Please explain purpose of un-numbered door between Stairs 115 and Vestibule 116.  Delete if unnecessary, and number/label if required.

Corrected by designer.

A1.1
Please identify where to find the wall section cut by 1/A1.1/A3.1 on west exterior wall of Cage area.  Depictions on Sheet A3.1 are for interior walls.

Will be reviewed by Architect and corrected by designer.

CUT HAS BEEN CORRECTED.

**A1.1
Indicate on this sheet the extent of enlarged plan details for toilet rooms. 

Corrected by designer. 



Repeat; Please show on the overall drawings where the enlarged drawings for toilet rooms and stairs are located.

Dashed border reference added to drawings.

A1.1
Provide an enlarged detail of Stair 115 and Vestibule 116.

Corrected by designer.

Shown as key notes.

A1.2
Revise the sheet number from ‘A1.1’ to ‘A1.2’.

Corrected by designer.

A1.2
Identify the thin line that encircles the second floor plan, approximately 1.5 feet away from the walls on the west, north, and east sides, and over 20 feet away on the south side.

Corrected by designer, labeled as overhang.

A1.2
We suggest that this sheet is a better place than Sheet A1.1 to show the window schedule, since there are no windows on the first floor.

Corrected by designer.

A1.2
Delete one ‘p’ from ‘RIVER OPPS CONTROL WATCH’ here and on the Room Number Schedule on Sheet A1.1.

Corrected by designer.

**A1.2
Show extent of adjacent Building 2441.

Corrected by designer.

Has been corrected.

Repeat:  Please indicate location of adjoining Building 2441 on this drawing.

Extent of Bldg. 2441 added to drawing.

A1.2
It appears that the south window in the west wall of Room 210 may need to be re-located due to conflict with adjacent Building 2441.

Will be reviewed by Architect.

WINDOW LOCATION HAS BEEN ADJUSTED, SEE BUILDING SECTION C ON SHEET A1.5.

A1.2
Finish Schedule – Refer to RFP Part 4, Section C10, Paragraph C102001 1.2.1 Sound Insulated Doors and Frames.  This paragraph directs the D/B Contractor to “provide sound insulated doors and frame assemblies into rooms requiring wall assemblies to be sound insulated with a Sound Transmission Class (STC) rating as required.  The STC rating for the door and frame assembly shall be not less than the wall assembly STC rating.”  The intent of the RFP was to require specific STC ratings for walls in specific rooms – not for all rooms.  Door/frame assemblies in rooms with a specified STC are to be sound insulated in accordance with the paragraph above.  Other doors/frame assemblies do not need to be sound insulated.  Please correlate the Finish Schedule on this sheet with the Door Schedule to make sure that all door/frame assemblies in walls requiring an STC rating are rated accordingly.

Will be reviewed by Architect and corrected by designer.

SCHEDULES HAVE BEEN CORRELATED.

A1.2
Finish Schedule – Wall finish for Entry should be IRWT/EP.

Corrected by designer.

Corrected on Finish Schedule, Sheet A1.7.

A1.2
Finish Schedule – The RFP calls for the floor finish in CSS to be CPTT-1, since this is office space.  The Schedule indicates concrete. 

Discussed at recent review meeting, User prefers concrete.

A1.2
Finish Schedule – The RFP called for a GWB ceiling for the Entry.   This was to avoid placing acoustical tile in the ceiling at frequently-used entrances where they will be subjected to high humidity, which could cause the tiles to sag.  The Finish Schedule shows acoustical ceiling tile (ACT) at entrances with a finished ceiling.  It might be acceptable to leave ACT as the finish for Entry 102 because of infrequent use, but we feel the GWB should be used at Vestibule 116, and metal panels on the soffit at Side Entry 104.

Discussed at recent review meeting, ACT deleted, metal panels to be used at 104.

A1.2
Finish Schedule – Please provide recessed mats at all entrances in accordance with the RFP.  

Corrected by designer.

A1.2
Finish Schedule – The RFP (see Part 3, Page 26) called for the walls around all telecommunications rooms to extend to the structure above.  Please review the Room Requirements in Part 3 of the RFP to ensure that you have accurately identified all rooms that are required to have walls extend to the structure above. 

Will be reviewed by Architect.

EXTENSION OF WALLS TO STRUCTURE IN ACCORDANCE WITH THE RFP HAS BEEN ADDED TO THE FINISH SCHEDULE.

Sheet A1.7

A1.2
Finish Schedule – The Coffee Mess was identified as part of the River Ops Control Watch Station on Page 35 of part 3 of the RFP.  The counter for the Coffee Mess is required to be a minimum of 12 feet long and is to consist of base cabinets and wall cabinets.

Corrected by designer.

A1.3
Suggest moving the “Detailed Building Requirements (Main Wind Force Resisting Components)” to one of the Structural Drawings.

Corrected by designer.

A1.3
Show connection detail of the 6” CMU wall to the steel frame. 

Detail being developed by engineering staff in coordination with Met. Bldg. Provider.

SEE MASONRY DETAILS ON SHEETS S3.1, THRU S3.4.

Section “T” Sheet S3.1

Section “S” Sheet S3.1

Section “X” Sheet S3.3

Section “W” Sheet S3.3

Section “AA” Sheet S3.3

5 & 6 Sheet A1.4

**A1.3
Show through-wall flashing at intermediate locations, steel stiffening angles, control joints and/or expansion joints, and other information relevant to construction of the CMU wall.

Details being developed by Architect.

SEE EXPANDED ARCHITECTURAL AND MASONRY DETAILS THROUGHOUT PLANS.

Sheet A1.3

9, Sheet A1.4

Det. 10, Sheet A1.5

12 & 13, Sheet A1.20

26 & 27, Sheet A1.21

20, 21, &22, Sheet A1.22

8, Sheet A1.23

Control Joint Details, Sheet 53.2

Drawings are more informative than before, but still do not show construction of through-wall flashing correctly.  It is important to minimize water intrusion for through-wall flashing in masonry (CMU) to actually penetrate into the horizontal mortar joints.  Revise all details where through-wall flashing is present/required to indicate this. Through-wall flashing is mentioned in the text of section 04 20 00, but installation is not described.  Its installation is not described in Section 07 60 00, either.  Please add a description of the installation of through-wall flashing.

Detail and installation of flashing shown in shop drawings from the manufacturer on CD under “Masonry Submittals”, page 32.

A1.3
Top left detail – Number this detail.  Identify location of through-wall flashing.  Identify the location of the insulation between the wythes of this wall system.  Provide a minimum of 1” actual dimension air space, not including insulation space, between wythes in accordance with RFP Part 4, Section B20, Paragraph B201001 1.1.3.  Provide bituminous dampproofing in accordance with RFP Part 4, Section B201002 1.1.1, not ‘Tyvek’ as indicated on this drawing.

Details being developed by Architect. Tyvek has been deleted.

SEE UPDATED DETAILS IN CURRENT DRAWINGS IN ACCORDANCE WITH ABOVE COMMENT, INCLUDING INCLUSION OF BITUMINOUS DAMPROOFING.

A1.3
Right center detail – Number this detail.  Identify location of through-wall flashing.  Identify the location of the insulation in this wall system.  Show ‘1/2” Densglass Gold Sheathing’ indicated in Section A in this detail.  Provide bituminous dampproofing in accordance with RFP Part 4, Section B201002 1.1.1, not ‘Tyvek’ as indicated on this drawing.

Details being developed by Architect. Tyvek  and Densglass have been deleted.

SEE UPDATED DETAILS AS PER ABOVE RESPONSE.

A1.3
Section A – Label rooms in this section.  Indicate how you intend to address the juncture of the steel frame and the acoustical ceiling.  The ceiling is to be flat; there shall be no inclined areas.  Identify the meaning of note indicating ‘6” CMU @ 8” O.C.’ at the bottom left of this section.  Provide detail of area around and construction of ‘cast stone lintel.’  Identify lines below perimeter beam at inside face of 6” CMU.  Verify that 6” CMU will span 25 feet vertically.  Indicate Building 2441 in the right side background.  Provide graphic depiction of rigid insulation within the roof system.

Section being revised by Architect and designer; 6” CMU has been replaced with 8” CMU. Cast stone lintel detail will be provided.

SEE UPDATED DETAILS INCLUDING CAST STONE DETAIL ON  SHEET A1.3.

Has been corrected.  R-19 (nominal 6”) being provided in between purlins.

A1.3
Provide background and derivation for U-Factors and R-Values indicated at top of this sheet. 

Calculations to be provided by engineering staff.

SEE EXTERIOR WALL THERMAL RESISTANCE REPORT IN THE CALCULATIONS.

A1.4
Remove the north arrow from this building section and label it as Section B.

Corrected by designer.

A1.4
Indicate walls that extend to roof above – generally, the “10’ Stud Walls” indicated are not correct.

Corrected by designer.

A1.4
Provide details at the roof overhang at each end of this section.

Detail to be provided after coordination with Met. Bldg. Provider.

UPDATED DETAILS PROVIDED ON SHEET A1.23.

A1.4
Top left detail – Number this detail.  Identify location of through-wall flashing.  Identify the location of the insulation between the wythes of this wall system.  Provide a minimum of 1” actual dimension air space, not including insulation space, between wythes in accordance with RFP Part 4, Section B20, Paragraph B201001 1.1.3.  Provide bituminous dampproofing in accordance with RFP Part 4, Section B201002 1.1.1, not ‘Tyvek’ as indicated on this drawing.  Verify that 6” CMU conforms to the physical construction requirements cited on RFP Part 3, Page 15 describing construction enclosing the Armory.

Detail being revised by Architect. Tyvek and 6” CMU have been deleted.

A1.5
In Section C, please indicate aspects of the west wall of the space, including windows on 2nd floor of building 2440.

Corrected by designer.

A1.5
Suggest moving the “Detailed Building Requirements (Main Wind Force Resisting Components)” to one of the Structural Drawings.

Corrected by designer.

A1.5
Indicate extent of coiling doors, bollards, and other features.

Corrected by designer.

A1.5
See comments on Sheets A1.3 and 1.4 concerning issues with detail on this sheet.

Corrected by designer.

A1.5
Provide background and derivation for U-Factors and R-Values indicated at top of this sheet.

Calculations to be provided by engineering staff.

SEE EXTERIOR WALL THERMAL RESISTANCE REPORT IN THE CALCULATIONS.

A1.5
Provide graphic depiction of rigid insulation within the roof system.

Corrected by designer.

A1.5
Show ‘1/2” Densglass Gold Sheathing’ indicated in Section C in a detail.

Corrected by designer, Denglass deleted.

A1.5
Show profile of boat on trailer to help verify clearances.

Corrected by designer.

A1.6
Right Side Elevation – 25’-0” eave height depiction does not correspond to location of eave.  Correct ‘River OPPS’ at left portion of Right Side Elevation.  Elevation indicates use of 8” CMU Split Face; all previous drawings indicate this to be 4”. Please reconcile.  Is ‘vented metal soffit’ required in a vertical application?  Elevation indicates that there are 12 bollards, but only 10 are depicted.  Indicate gutters and downspouts.

Corrected by designer.

A1.6
Left Side Elevation – 25’-0” eave height depiction does not correspond to location of eave.  Elevation indicates that there are 12 bollards, but only 10 are depicted.  Elevation indicates use of 8” CMU Split Face; all previous drawings indicate this to be 4”. Please reconcile.  Indicate gutters and downspouts.  Identify ‘SL’ at bottom center of this elevation.

Corrected by designer. Gutter and downspout design being coordinated with Met. Bldg. Provider.

GUTTERS AND DOWNSPOUTS INDICATED ON A1.8, A1.9, AND A1.14.

A1.6
Both Elevations – Indicate location of control joints and/or expansion joints in the masonry.


Joints to be determined by Architect and shown by designer.

JOINTS INDICATED ON ELEVATIONS A1.8 AND A1.9.

**A1.7
Front Elevation – Provide a detail of bolting the stair platform to the building.  Provide a detail of the 12” x 4’ deep concrete pillar for stair column and attachment of the two.

Detail to be provided after coordination with engineering staff.

DETAILS SHOWN ON SHOP DRAWING FOR BUILDING 2440.

Repeat:This response mentions that the information requested is indicated on Shop Drawings.  Please provide these Shop Drawings for our review.

Shop Drawings on CD under “Submittals”, Exterior Stairs.

A1.7
On the Rear Elevation, provide details of connections of stair elements.

These stairs have been deleted by the User.

A1.7
On the Typical Handrail/Guardrail Detail, refer to UFAS, not ADA or ADAAG.  Also, refer to UFAS Figure 19(c) and 19(d) for the correct depiction of handrail extensions at bottom and top of stair runs and modify this drawing to comply.  

Corrected by designer.

A1.7
Both Elevations – Indicate location of control joints and/or expansion joints in the masonry.


Will be corrected by designer after review by Architect.

MASONRY JOINTS INDICATED ON ALL ELEVATIONS.

A1.8 and A1.9
Remove square footages from this sheet.

Corrected by designer.

A1.8 and A1.9
Indicate room names on the plan view instead of providing a Room Number Schedule.

Corrected by designer.

A1.8 and A1.9
Providing a graphical materials legend instead of the abbreviation legend provided.

Will be corrected by designer after review with Architect.

GRAPHIC MATERIALS LEGEND INDICATED ON SHEET A1.7,A1.10, AND A1.11.

A1.9
Verify extent of acoustical ceiling tile.   

Will be corrected by designer after review with Architect.

VERIFIED AND SHOWN ON SHEETS A1.10 AND A1.11.

A1.10
Locate soap dispensers (Item #5) above lavatories, not between lavatories as shown, so when they drip, they don’t drip over the floor.  

Corrected by designer.

A1.10
Delete reference to ADA clear space, since UFAS is the governing code for accessibility in DOD facilities. 

Corrected by designer.

A1.10
In Female Head 212 – Center mirror above the lavatory.

Corrected by designer.

A1.10
In Head 109 – The Grab Bar designation should be ‘4,’ not ’10.’  Also, make sure that Item 1 does not encroach on the required clear space at the lavatory in this room.  Ensure that the door does not swing into the required clear space at the toilet in this room. Swinging the door out is an option.

Corrected by designer.

A1.10
Verify sizes of Items 8 and 9 in Rooms 109 and 212, and make sure Item 9 is reachable by a disabled person in Head 109.

Corrected by designer.

**A1.10
Verify that shower stall in Shower 108 complies with the size requirements for this item in UFAS.  It does not appear that the shower shown complies with either Fig. 35(a) or 35 (b).

Corrected by designer.

Has been corrected.

Repeat:  Provide all dimensions, including depth, for shower stall in Room 108 on Sheet A1.12.  The dimension to the left of the shower, 3’-2” does not represent the actual clear width of the shower, and the depth is not dimensioned anywhere.

Dimensions added to drawings.

A1.10
Show locations of floor drains in the rooms indicated on this sheet.

Will be corrected by designer after review with Mechanical Engineer.

FLOOR DRAINS SHOWN ON ARHITECTURAL, STRUCTURAL AND MECHANICAL SHEETS.

A1.10
Indicate dimensions of toilet partitions and urinal screens.

Will be corrected by designer after review with Architect.

DIMENSION SHOWN ON ENLARGED PLANS, SHEET A1.12 AND INTERIOR ELEVATIONS SHEET A1.16.

A1.10
We could not locate Item #14 in Rooms 10 or 112.

Corrected by designer.

A1.10
Provide mirror in Shower 108 in accordance with RFP (Part 3, page 19).

Corrected by designer.

A1.10
Provide screening for the entrance to Male Head 211.  Everyone leaving the stairs will have a direct view into the first toilet stall when the door to the head is ajar.

Corrected by designer after review with Architect.

A1.10
Why are plumbing chases behind toilets and urinals different sizes (10” in Rooms 111 and 109 and 1’-5 ¼” in Rooms 211 and 212)?  

4” or 10” is typical, the larger chase size is to conceal structural steel members.

A1.11
Correct sheet number from ‘A1.1’ to ‘A1.11’.

Corrected by designer.

A1.11
Identify Building 2440 and 2441.

Corrected by designer.

A1.11
Is it your intent to cover the stairs?  No cover is indicated on stair elevations.

The intent is to cover the stairs; elevations will be corrected by designer.

ELEVATIONS CORRECTED, SEE SHEET A1.9.

A1.11
Identify heavy horizontal line near north end of Building 2440.

Deleted by designer.

A1.11
Show gutters on this drawing.

Will be corrected by designer after review with Met. Bldg. Provider.

GUTTERS HAVE BEEN SHOWN ON ALL ELEVATIONS.

A2.1
Identify how personnel are to access this building, particularly the center bay.

Wire mesh partitions have been deleted by User.

Has been corrected.

A2.1
Correct the callout (A1.2/A1.3 portion of callout) for Section A.

Corrected by designer.

A2.1
Bollards near bows of boats were shown in the RFP to protect the stairs and platform between boats.  If it is determined that these stairs and elevated walkways are not necessary, the bollards may not be necessary, either.

Bollards and walkways have been deleted by User.

A2.2
Indicate height at top of clerestory.

Corrected by designer.

A2.2
Show gutters and downspouts.

Will be corrected by designer after review with Met. Bldg. Provider.

GUTTERS AND DOWNSPOUTS HAVE BEEN SHOWN ON ALL ELEVATIONS.

A2.2
Section A was cut through a coiling door on Sheet A2.1.  Correct the section on this sheet to show this.

Corrected by designer.

Has been corrected.

A2.2
Show platform on long side opposite the doors as well as rear exit doors and exterior stairs.

Platform will be shown by designer; other items have been deleted by User.

SEE UPDATED SHEET A2.2.

**A2.2
Show through-wall flashing at intermediate locations, steel stiffening angles, control joints and/or expansion joints, and other information relevant to construction of the CMU wall.

Details will be determined by Architect and shown by designer.

SEE EXPANDED ARCHITECTURAL AND MASONRY DETAILS THROUGHOUT PLANS.

Has been corrected.

Drawings are more informative than before, but still do not show construction of through-wall flashing correctly.  It is important to minimize water intrusion for through-wall flashing in masonry (CMU) to actually penetrate into the horizontal mortar joints.  Revise all details where through-wall flashing is present/required to indicate this. Through-wall flashing is mentioned in the text of section 04 20 00, but installation is not described.  Its installation is not described in Section 07 60 00, either.  Please add a description of the installation of through-wall flashing.

Detail and installation of flashing shown in shop drawings from the manufacturer on CD under “Masonry Submittals”, page 32.

A2.2
Show profile of boat on trailer to help verify clearances.

Corrected by designer.

A2.2
Top left detail – Number this detail.  Suggest taking this detail at bottom right portion of Section A and mirroring all items in the detail.  Identify location of through-wall flashing.  Identify the location of the insulation between the wythes of this wall system.  Provide a minimum of 1” actual dimension air space, not including insulation space, between wythes in accordance with RFP Part 4, Section B20, Paragraph B201001 1.1.3.  Provide bituminous dampproofing in accordance with RFP Part 4, Section B201002 1.1.1, not ‘Tyvek’ as indicated on this drawing.

Detail will be corrected similar to detail on A1.3

DETAIL HAS BEEN CORRECTED.

A2.3
This drawing indicates use of 8” CMU Split Face but the detail on Sheet A2.2 indicates this CMU to be 4.” Which is correct?

Corrected by designer, to be 4”.

A2.3
Indicate gutters and downspouts on these elevations.

Will be corrected by designer after review with Met. Bldg. Provider.

GUTTERS AND DOWNSPOUTS HAVE BEEN ADDED TO ALL ELEVATIONS.

A2.3 and A2.4
Both Elevations – Indicate locations of control joints and/or expansion joints in the masonry.

Will be indicated by designer after review with Architect.

SEE MASONRY DETAILS ON SHEETS S3.1, THRU S3.4.

A2.4
Why change scale of elevation drawings (from Sheet A2.3)?

Corrected by designer

¼” scale is appropriate.

A2.4
Indicate gutters and downspouts on these elevations. 

Will be corrected by designer after review with Met. Bldg. Provider.

GUTTERS AND DOWNSPOUTS HAVE BEEN ADDED TO ALL ELEVATIONS.

A2.5
Indicate gutters on this drawing.

Will be corrected by designer after review with Met. Bldg. Provider.

GUTTERS AND DOWNSPOUTS HAVE BEEN ADDED TO ALL ELEVATIONS.

A3.1
Where do you intend to use this 2-hour wall?

Corrected by designer, 2-hour wall not needed.

A3.1
Provide UL number for Wall Section 2. (Repeat Comment from Concept Submittal).

Architect will provide UL number.

UL NUMBERS INDICATED ON SHEET A1.6.

A3.1
Neither wall section will possess the (2-hour or 1-hour) rating indicated unless it extends to structural floor or roof above and penetrations are firestopped.  Please clarify this on the drawing. (Repeat Comment from Concept Submittal).

Wall section will be shown in full as demised.

DRAWING CLARIFIED, SEE SHEET A1.6.

Architectural Specs
Comments

Table of Contents
The Table of Contents only lists sections through Division 9.  Please list all sections.

In general, specification manual will be submitted at pre-final in Specsintact format. Proposed table of contents will be provided prior to that as discussed at recent review meeting.

SPECIFICATION MANUAL SUBMITTED AT PRE-FINAL IN SPECSINTACT FORMAT. COMMENTS FROM THAT REVIEW WILL BE ADDRESSED IN THE FINAL SUBMITTAL.


General
All references to the RFP in these comments relate to Part 4, unless noted otherwise.

General
It appears that many of the requirements for products described in the RFP have not been incorporated.  Most specification sections read as generic specifications and have not been edited to reflect the requirements of this project.  This makes it difficult for a reviewer or contractor to wade through non-applicable information to find a product intended for the project.  These specifications should be re-edited.

General
There appear to be many missing specifications that need to be provided.  Please review the work involved in the project and add additional sections necessary to completely define the products and procedures.

General
Section 02360 from Part 5 of the RFP needs to be included in the project.  It should be included without changes.

042000
Paragraph 1.2.A and others throughout this section – Delete all references to materials that are not used on this project, such as concrete brick, face brick, building (common) brick, hollow brick, and limestone.


Has been corrected in revised/updated specifications.

042000
Paragraph 1.2.B – This paragraph refers to spec sections, “Water Repellants,” “Joint Sealants,” and “Louvers and Vents” in other divisions that are not provided.  Provide these sections.


Has been corrected in revised/updated specifications.

042000
Paragraph 1.5 – Refer to RFP, Part 4 Paragraph B20 1.7 for all construction submittal requirements, and list all submittals that apply to masonry, including Test Reports (SD-06) and Certificates (SD-07).

042000
Delete references to materials such as brick that are not used on the project.

042000
Paragraph 3.5 – Verify with structural engineer that masonry is to be attached to structural members.

042000
Paragraph 3.8.C.2 – Verify limiting height of grout pour.

**042000
Paragraph 3.3 – Describe installation of bituminous dampproofing, rigid insulation, air space, and facing materials.  See B201001 in the RFP.


Hohmann & Barnard, Inc., veneer anchors to be installed in accordance with plans, specs & reviewed shop drawings.  Please see attached shop drawings.


Repeat:This response mentions that the information requested is indicated on Shop Drawings.  Please provide these Shop Drawings for our review.

Detail and installation of flashing shown in shop drawings from the manufacturer on CD under “Masonry Submittals”.

**04 20 00
Through-wall flashing is mentioned in the text of section 04 20 00, but installation is not described.  Its installation is not described in Section 07 60 00, either.  Please add a description of the installation of through-wall flashing.

Detail and installation of flashing shown in shop drawings from the manufacturer on CD under “Masonry Submittals”, page 32.

Page 18 of 18

