Paul,

My comments are listed below. Hard copy to follow.

PLANS REVIEW, SOF RIVERINE AND COMBATANT CRAFT OPERATIONS FACILITY
(FY2008 MILCON P-210)

Reference: (a) CFR 1910.305(j)(7)

Observation (1): The Boat Storage Building 2442 has slots for 12 boats.
A raised platform is positioned at or above the stern area of stored
boats. It is unknown if work processes will take place within these
spaces.

Recommendation (1): If battery maintenance or hazardous material use
will occur within Building 2442, provide emergency eyewash stations.
Depending on the type of battery: reference (a) requires provisions be
made for the diffusion/ventilation of gases from storage batteries.

RESPONSE:

No battery maintenance to be performed in Boat Storage Building 2442. Battery maintenance to be performed in Maintenance Area / Staging Building 2441, which has two emergency eyewash stations and ventilation.

Observation (2): The Operations Building 2440 and the Boat
Maintenance/Staging Building 2441 are attached to each other. Work
process requiring hazardous material use within the Boat
Maintenance/Staging Building 2441 spaces could result in vapors/fumes
entering the adjacent spaces of Building 2440. Areas of concern include
the Lobby (103), CSS (106), Armory (107) and Vestibule (116). The plans
specify a 6000 CFM exhaust fan for building 2441. Details of the
operations of this fan were not available.

Recommendation (2): To prevent contaminants from entering building
2440, ensure that building 2441 always operates under negative pressure
relative to building 2440.

RESPONSE:

Building 2440 will act in positive pressure relative to Building 2441.

The exhaust fan is thermostatically controlled with a user interface (override) for manual operation if the thermostat does not engage fan operation and ventilation is needed.

Donald Krehely Jr. CIEC, CMC, CMRS
Supervisory Industrial Hygienist
Naval Hospital Pensacola
Work 850-452-5666 (New Number)
Cell 850-375-0235
Fax 850-452-5260
donald.krehely@med.navy.mil