	DESIGN COORDINATION AND REVIEW COMMENTS
NAVFAC Southeast
	JOB ORDER NO.


	COMMENTS BY/Discipline
David Melendez/Civil Eng
	CODE

GC IPT 
	PHONE

(904) 542-6781
	DATE

13 Jul 09

	PROJECT TITLE AND LOCATION
	
	TYPE OF REVIEW

	P210 SOF Riverine & Combatant Craft Operations Facility
	
	65%

	Stennis, MS
	x
	100% (Pre-Final)

	
	
	FINAL

	
	
	OTHER

	DWG. NO. OR

PAR NO.
	COMMENTS

(MAKE GENERAL COMMENTS BEFORE SPECIFIC COMMENTS)
	ACTION TAKEN
(& REASONS WHERE SIGNIFICANT)



	General
	· Provide NAVFAC Drawing Numbers in Final Submittal.---

· Where is the survey layout indicating the existing site conditions, existing grades, contours, etc?
	1.NAVFAC dwg numbers distributed.

2.Refer to RFP for Survey information. Existing site conditions and contours per survey are shown on sheets C5.1/C5.2.

	T-2 
	· Title Block should read “IPT Gulf Coast” not “IPT South Atlantic”
	Corrected.

	C1.0
	· Recommend changing “isles” to “aisles” in note 4 of parking lot section.
	Corrected.

	C1.1
	· Provide graphic scale in addition to numerical scale. Typical.

· Verify scale 1’=60’, should probably be 1”=60’.  Several Civil sheets have similar scale errors. Please correct.

· Reference to motorcycle parking lot sheet C3.3 is incorrect.

· Provide parking stalls dimensions.

· Provide bicycle rack details.

· Use bubble diagrams to link notes to details.

· Provide striping for truck pad (4 trucks and trailers)

· Provide additional coordinates for parking lot and other key elements such as roads, entrances…

· Reference: Sheet C3.3 does not contain details on fuel efficient vehicle signs. Typical reference.

· Please verify turnstile is ADA compliant.


	1.Graphics are shown near Title blocks for all sheets.

2.Corrected.

3.Corrected. Reference changed to C3.4.

4.Provided on C1.2.

5.Rack N.I.C.

6.Will provide bubbles where appropriate.

7.Added striping to C1.1/C1.2

8.Additional coordinates will be provided.

9.Corrected to read C3.4 for detail.

10.Turnstile detail is per RFP.

	C1.4
	· Provide PVC coating for what? Fence fabric?


	Note is on C1.5, #3.



	C1.5
	· Detail 7 & 8, 2” max space between fence fabric and grade line, contradicts Detail 1 & 2 of page C1.4, 1” max.
	2” required @ C1.5 for rolling gate.

	C2.1
	· Is the finished floor elevation 16’? Please clarify.

· Provide additional spot elevations around the building (outside). Provide finished contours.

· Provide swale details.

· Grading shall comply with UFC 3-200-10N Section 2-2.3 Surface Storm Drainage (July 06 or most recent). Current plan does not provide enough information to verify compliance.

· Provide the 100 yr Flood Elevation.
	1.F.F.E. 16’, added to drawings.

2.Additional spot elevations have been added.
3.See swale schedule this sheet.

4.

5.B.F.E. 14.0’ provided on drawing.

	C2.2
	· Why do some elevations have # in front of them? Please clarify.

· Provide invert elevations on both sides of pipes/culverts. Typ.
	Refer to C1.0 symbol legend, # indicates invert.

Added to plans.

	C3.1
	· I did not find 8’ sidewalk w/curb detail on S4.3
	Sidewalk detail on S4.3, no curb.

	C3.2
	· No intermediate expansion joints noticed. Please reconsider including additional expansion joints.
	Disagree, joints provided per RFP requirements.

	C3.4
	· Edit notes on detail 37; not a H.C. parking space. Same note applies to detail 39 and 40.
	Corrected to read “parking space, typ.”

	C5.1
	· Are these existing or proposed grades?

· Please verify location of note “Chain Linked fence for temporary entrances” (x,y,=2,C)
	1.Existing.

2.Verified.

	C6.1
	· Provide details of intersection of water line with sanitary lines, for all intersections.

· Water line from the existing water main all the way to the potable water line (CW) should be considered a potable water line and should be labeled as such.

· Post indicator valve should be relocated to Fire Protection Line.
	1.Pipe Intersection detail added to C6.1.

2.Corrected to read “PW”.

3.Relocated, and added 2 additional post indicator valves.



	C6.5
	· Detail S3 makes reference to sheet C-4, sheet not provided.

· Detail 49 makes reference to sheet C-2; sheet not provided.
	1.Replaced with new detail. Reference removed.

2.Reference deleted.

	
	Notes: Project not set up in Dr Checks. Comments in red are critical.
	

	
	
	

	
	
	

	
	
	


SHEET   1   OF   2    SHEETS

