	PROJECT REVIEW
COMMENTS

	Project No.  0LA2083
	     Agency:     USDA-APHIS
     Realty PM:  Sylvia Cabello

	
	Location:   Kenner, LA
	Building Name:

	
	Review Phase:   50% CD Review
	Date: 1/26/2012
	Page 1 of 2

	Reviewer: D. WONG
	Organization: GSA 

	Comm.

No.
	page No.
	COMMENTS

ARCH__ CIV __ STRC __ MECH      ELEC _X_FIRE __  OTHER ___
	RESOLUTIONS (BY A/E)

	 1
	 E-1
	ALL UNUSED WIRE AND CONDUIT SHALL BE REMOVED AS POSSIBLE.
	Comment has been revised to state: “EXISTING ELECTRICAL SERVICE AND EXISTING METERS ARE NOT TO BE USED FOR THIS PROJECT.  EXISTING CONDUIT FROM METER TO SUITE TO REMAIN, THERE ARE NO EXISTING WIRES FROM METER TO SUITE."

	 2
	 E-1
	ALL UNUSED CIRCUITS SHALL BE INDICATED AS “SPARE” ON PANELBOARD DIRECTORIES.
	ALL PANELS SHOW SPARE BREAKERS WHEN NOT ALLOCATED.

	 3
	 E-1
	SHOW CIRCUIT NUMBERS FOR LIGHTS AND OUTLETS.
	CIRCUIT NUMBERS HAVE BEEN ADDED.

	 4
	 E-1
	SHOW CIRCUIT NUMBERS FOR MECHANICAL EQUIPMENT.
	CIRCUIT NUMBERS HAVE BEEN ADDED.

	 5
	 E-1
	REFERENCE TO BREAK ROOM P-12: GFI TYPE DUPLEX RECEPTACLES SHALL BE MOUNTED ABOVE COUNTER.
	COMMENT #11 HAS BEEN ADDED TO INSTALL RECEPTACLES 6IN ABOVE COUNTERTOP.

	 6
	 E-1
	REFERENCE TO INSPECTION ROOM P-5 AND COMBINED LABS ROOMS P-20 AND P-21: SHOW DUPLEX RECEPTACLES MOUNTED HEIGHT.
	COMMENT #11 HAS BEEN ADDED TO INSTALL RECEPTACLES 6IN ABOVE COUNTERTOP.

	 7
	 E-1
	REFERENCE TO UNISEX RESTROOM P-2, WOMEN’S ROOM P-13 AND MEN’S ROOM P-14: GFI TYPE DUPLEX RECEPTACLES SHALL BE MOUNTED ABOVE COUNTER.
	COMMENT #11 HAS BEEN ADDED TO INSTALL RECEPTACLES 6IN ABOVE COUNTERTOP.

	 8
	 E-1
	(1) CLARIFY WHETHER DISCONNECT SWITCHES ARE REQUIRED FOR MECHANICAL EQUIPMENT. IF SO, PLEASE SHOW ON DRAWING.
(2) SHOW CHARACTERISTIC OF DISCONNECT SWITCHES. SUCH AS VOLTAGE, AMP. RATING, NUMBER OF PHASE, NUMBER OR WIRE, FUSIBLE OR NON-FUSIBLE ETC.
	A disconnect schedule has been added to the plan.

	 9
	 E-1
	REFERENCE TO GENERATOR:
(1) PROVIDE WALK-IN ACOUSTIC ENCLOSURE AND JACKET WATER HEATER TO ENSURE RELIABLE STARTING IN COLD WEATHER.

(2) PROVIDE CIRCUITS FOR JACKET WATER HEATER AND BATTERY CHARGER.
(3) AUTOMATIC TRANSFER SWITCHES SHALL INCLUDE A BYPASS ISOLATION SWITCH THAT ALLOWS MANUAL BYPASS OF THE NORMAL OR EMERGENCY SOUREC TO INSURE CONTINUE POWER TO EMERGENCY CIRCUITS IN THE EVENT OF SWITCH FAILURE OR REQUIRED MAINTENANCE.
	GENERATOR NOTE #2 HAS BE REVISED TO STATE THAT THE GENERATOR SHALL BE HOUSED IN A WALK-IN SOUND ATTENUATED ENCLOSURE WITH LIGHTING FOR MAINTENANCE OF GENSET.

	 10
	 E-2
	REFERENCE TO ELECTRICAL RISER DIAGRAM:
(1) IDENTIFY WHICH BREAKER NEEDS TO BE UPGRADE AS NOTED.

(2) IDENTIFY WHICH METER(S) IS/ARE FOR SUITE 13 AND SUITE 14.

(3) ARE THERE TWO SERVICES FOR THIS FACILITY?
	The electrical riser has been revised to include new load.  A single meter system with a new feeder and all associated equipment is to be new.

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	 
	

	
	
	
	

	
	
	 
	

	
	
	
	

	
	
	
	

	
	
	
	


