	PROJECT REVIEW
COMMENTS

	Project No.  0LA2083
	     Agency:     USDA-APHIS
     Realty PM:  Sylvia Cabello

	
	Location:   Kenner, LA
	Building Name:

	
	Review Phase:   50% CD Review
	Date: 2/1/12
	Page 1 of 1

	Reviewer: Garlick, Jason
	Organization: GSA 

	Comm.

No.
	page No.
	COMMENTS

ARCH__ CIV __ STRC __ MECH      ELEC _ _FIRE __  OTHER ___
	RESOLUTIONS (BY A/E)

	 1
	 P-1 General Notes, Water Piping
	Recommend Type K soft copper for below grade applications on water supply lines
	COMMENT FOR THE TYPE OF COPPER BELOW GRADE HAS BEEN REVISED TO TYPE ‘K’

	 2
	 P-1
	No water hammer arrestor is shown on supply lines in the Water and Sanitary Sewer detail. 
	ITEM ‘E’ OF THE GENERAL NOTES FOR WATER PIPING HAS BEEN AMENDED TO INCLUDE WATER HAMMER ARRESTORS AT HOT AND COLD WATER PIPING FIXTURES.

	 3
	 A401
	Recommend noting/specifying UL listed assemblies for rated partitions as a basis of design. Fire rated partition detail shown on A401 is not consistent with typical UL listed assemblies. Head of wall fire stopping and framing support to roof deck not shown etc. 
	NOTES UPDATED SPECIFING UL LISTED ASSEMBLIES.  DETAILS UPDATED TO COMPLY.

	
	A202
	Note designations not legible on floor plans. Particularly doors. Please provide legible documents.
	UPDATED NOTES TO BE LEGIABLE.

	
	
	Verify server room meets Special Requirements (pgs.5-7) and TIA/EIA 568 as required in the SFO. (Size, dedicated power panel and grounding, positive pressure, etc.) Take into account space needed for govt furnished equipment.  
	ITEM 12 HAS BEEN ADDED TO THE POWER PLAN’S ELECTRICAL SHEET NOTES:”ALL COMPUTER ROOM OUTLETS MUST BE DEDICATED & HAVE AN ISOLATED GROUND FOR EACH CIRCUIT.” A dedicated power panel has been added.
  

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	 
	

	
	
	
	

	
	
	 
	

	
	
	
	

	
	
	
	

	
	
	
	


