	PROJECT REVIEW
COMMENTS

	Project No. 0LA2083
	Agency:     USDA-APHIS
Realty PM:  Sylvia Cabello

	
	Location: Keener, LA
	Building Name: 

	
	Review Phase: 50% CD Review
	Date: 01/31/2012
	Page 

	Reviewer: Kenneth Kwan
	Organization: GSA – 7PCE 

	Comm.

No.
	page No.
	COMMENTS

ARCH__ CIV __ STRC __ MECH  x  ELEC __ FIRE __  OTHER ___
	RESOLUTIONS (BY A/E)

	1
	M-1
	Mechanical Plan.

Provide and indicate Room Name and Room Number for each space/room.  


	Room names and numbers have been added.

	2
	M-1
	Mechanical Plan.

Provide and indicate air conditioning system, with heating, for Warehouse area to maintain area at 85 degree F in summer, and 55 degree F in Winter, as required per Special Requirements (SR) of the UDSDA-APHIS, paragraph 6.a. Ventilation with exhaust fan EF-6 as shown will not be able to provide the room temperature as required. 


	This requirement has been removed from the warehouse.

	3
	M-1
	Mechanical Plan.

Coordinate and verify with architectural and structural design that the standing metal panel roof for this building is suitable for the installation of HVAC Rooftop Unit, and that supports for units are provided in the structural design.   


	ROOF ON BUILDING IS AN R-PANEL EXPOSED FASTENER ROOF.  ROOFTOP UNIT SUBMITTAL WILL INCLUDE MOUNTING & FRAMING DETAILS BASED UPON SPECIFIC UNITS WEIGHT.

	4
	M-1
	Mechanical Plan.

Provide and indicate sizes for all supply, return and exhaust air ducts.  For exhaust air duct discharge to outside wall, provide and indicate the wall louvers and sizes of the louvers.  


	AIR DUCT SIZES HAVE BEEN ADDED.EXHAUST FANS WILL DISCHARGE THROUGH ROOF PENETRATION AND A DETAIL HAS BEEN PROVIDED.

	5
	M-1
	Mechanical Plan.

Delete the outside air intakes with ductwork from wall louvers as shown.  Rooftop units shall have outside air intake hoods/dampers as integral or optional part of the units.  


	OUTSIDE AIR INTAKES FOR RTU’S HAVE BEEN REMOVED.

	6
	M-1
	Mechanical Plan.

Revise HVAC design for Combined Labs Room for 100% exhaust (no return air from this room), as required per Special Requirements (SR) of the UDSDA-APHIS, paragraph 6.b.  This will require the use of exhaust fan and ductwork, and interlock with fume hood operation, so exhaust fan will not operate when fume hood is in operation, and vice versa. 


	THE HVAC DESIGN HAS BEEN REVISED FOR A UNIT TO SUPPLY 100% FRESH AIR, EACH ROOM WITH SUPPLY AIR FROM THIS UNIT HAS AN EXHAUST FAN AND ALL AIR IS TO BE EXHAUSTED.

	7
	M-1
	Rooftop Air Conditioning Schedule.

RTU-3 serving Combined Labs Room shall be sized to have minimum outside air equal to the larger of total supply air to room, or exhaust air from fume hood.  Note that the cooling and heating capacities of unit shall be sized to handle this minimum outside air load, in addition to room loads (building envelopment load, occupants load, lighting load, equipment load, etc.).  


	THE HVAC DESIGN HAS BEEN REVISED FOR A UNIT TO SUPPLY 100% FRESH AIR, EACH ROOM WITH SUPPLY AIR FROM THIS UNIT HAS AN EXHAUST FAN AND ALL AIR IS TO BE EXHAUSTED.

	8
	M-1
	Rooftop Air Conditioning Schedule.

RTU-2 serving Servers Rooms shall have reheat coil and humidifier for de-humidification and humidification control, to maintain rooms at 45% RH, per Special Requirements (SR) of the UDSDA-APHIS.  Revise Schedule to indicate these requirements.


	A REHEAT COIL AND HUMIDIFIER HAS BEEN ADDED TO THE SCHEDULE FOR THIS RTU.

	9
	P-1
	Water & Sanitary Sewer Plan.

Identify the EMS in Combined Labs Room as emergency shower and eyewash, as required per Special Requirements (SR) of the UDSDA-APHIS, paragraph 11.  Provide and indicate the tempered (mixed cold and hot water) water supply piping and sanitary sewer piping for it.  


	EMERGENCY SHOWER LOCATED IN C-2 WAREHOUSE SATISTFIES ALL EMS REQUIREMENTS FOR THIS SPACE. AS PER TELEPHONE CONFERENCE WITH USDA.

	10
	P-1
	Water & Sanitary Sewer Plan.

Provide and indicate the emergency shower and eyewash in Inspection Room P-5, as required per Special Requirements (SR) of the UDSDA-APHIS, Room-by-Room Requirement.  Provide and indicate the tempered (mixed cold and hot water) water supply piping and sanitary sewer piping for it.  


	EMERGENCY SHOWER LOCATED IN C-2 WAREHOUSE SATISTFIES ALL EMS REQUIREMENTS FOR THIS SPACE. AS PER TELEPHONE CONFERENCE WITH USDA. EYE WASH HAS BEEN ADDED.

	11
	P-1
	Water & Sanitary Sewer Plan.

Coordinate with architectural drawing to provide and indicate a wall-mounted drinking water cooler in Fitness Room P-16, as required per Special Requirements (SR) of the UDSDA-APHIS, Room-by-Room Requirement.  


	SHOWN. SEE A-202.

	12
	P-1
	Water & Sanitary Sewer Plan.

Coordinate with architectural drawing to provide and indicate a sink with gooseneck faucet and wrist blade in Location Room P-17, as required per Special Requirements (SR) of the UDSDA-APHIS, Room-by-Room Requirement.  


	SINK REQUIREMENTS FOR P-17 HAD BEEN REMOVED IN PREVIOUS REVIEW BY THE USDA.  NO CORRECTION MADE.

	13
	P-1
	Water & Sanitary Sewer Plan.

Coordinate with architectural drawing to provide and indicate a utility sink and floor drain in Warehouse C-2, as required per Special Requirements (SR) of the UDSDA-APHIS, Room-by-Room Requirement.  


	SHOWN. SEE A-202.

	
	
	
	

	
	
	---- End of Comments -----
	

	
	
	
	


