
SECTION 15290PRIVATE 


DUCTWORK INSULATION
PART 1
GENERAL

1.01
WORK INCLUDED

   
A.
Provide ductwork insulation and insulation jackets.

PART 2
PRODUCTS

2.01
INSULATION MATERIALS

A. Type A:  Fiberglass all service duct wrap, light density glass fiber insulation in roll form, faced with a reinforced foil/kraft laminate, meeting the requirements of ASTM C 553.  Duct wrap overlap shall be stapled and sealed with mastic coated fabric cloth.

B. Type B:  Fiberglass Aeroflex duct liner, resilient fibrous glass in blanket form, with a fire-resistant coating to bond with fibers of the airstream surface, meeting the requirements of ASTM C 1071 and complying with National Fire Protection Association Standard NFPA 90A.

2.02
ACCESSORIES AND ATTACHMENTS

A. Adhesives:  As recommended by insulation material manufacturer and complying with MIL-A-24179A.

B. Fire-Resistant Adhesive:  MIL-A-3316C, Classes 1 and 2, Grade A.

C. Bands:  19 mm (3/4 inch) wide, in one of the following materials compatible with jacket:

1. Stainless Steel:  ASTM A 666, Type 304.

2.03
VAPOR RETARDERS

A. Mastics:  Materials recommended by insulation material manufacturer that are compatible with insulation materials, jackets, and substrates.

B. Vapor-Retarder Mastics:  Comply with MIL-C-19565C, Type II; fire and water resistant.

PART 3
EXECUTION

3.01
DUCTWORK INSULATION SCHEDULE

	PRIVATE 
DUCTWORK TYPE
	INSULATION TYPE
	INSULATION THICKNESS (Inches)

	Supply Ducts
	A
	2

	Supply Ducts in Attics
	A
	3

	Supply Plenum
	B
	1

	Return Ducts
	A
	2

	Return Ducts in Attics
	A
	3

	Return Plenum
	B
	1

	Exposed Ductwork
	B
	1

	Exhaust Ducts (within 10 feet of exterior openings)
	A
	2

	Make-up Air Ducts
	A
	2

	Dryer Exhaust Ducts
	A
	2



END OF SECTION

La Quinta Inns, Inc.
15290 - 2
May 11, 2001

