
SECTION 16019PRIVATE 

EQUIPMENT AND CONDUIT IDENTIFICATION

PART 1
GENERAL

1.1
SUMMARY


A.
Section Includes:


1.
Nameplates.


2.
Labels.

1.2
GENERAL


A.
All electrical equipment and devices shall be identified by nameplates, name-tapes or labels.

PART 2
PRODUCTS

2.1
NAMEPLATES


A.
Nameplates shall be 4" x 1" x 1/8" thick white core, black face, plastic with engraved letters.  Attachment to equipment shall be done by means of screws.


B.
Nameplates shall be used for all major equipment such as switchboards, motor panelboards, motor control centers, panelboards (lighting, power and auxiliary) on each switch and starter in each panelboard, disconnect switches, relays, loose mounted motor starters, and on control panels serving fire alarm, security and public address system and motor circuits.

2.2
LABELS


A.
Labels (Stencils) shall be Brady, Westline or 3M and shall be color coded in accordance with ASA-Z34-1-53 "SAFETY COLOR CODE" to include system voltages, abbreviations of service, etc.  For example:  Telephone, Emergency, 120/208V, etc.

PART 3
EXECUTION

3.1
GENERAL


A.
In general, all exposed feeders, conduits, raceways, pull boxes, and junction boxes shall be identified.


B.
For conduit systems installed for future wiring installations all conduits and pull boxes, both exposed and above ceiling, shall be identified.


C.
Labels shall be used on all bare or smooth painted surfaces.  For rough textured surfaces, such as wrinkle painted surfaces or plastic materials where sticking labels would not be permanent, stencils or screwed on letters shall be used.

3.2
EQUIPMENT IDENTIFICATION


A.
Panelboard - Nameplate shall designate panel number and voltage. Nameplate shall be mounted on the inside of panel door when the panel is located in finished areas and on the front of door when located in mechanical equipment rooms; typewritten branch circuit connection sheet shall be inserted within the card holder provided by panelboard manufacturer.  Branch circuit designations shall be made only after the load balancing of the panelboards has been completed.


B.
Disconnect Switches and Motor Starters - Nameplates shall describe the equipment to be controlled and power circuit number, for example: "Chilled Water Pump CP-1, Panel 1P1-4", etc.


C.
Push button Stations - Name-tape shall identify the equipment controlled.


D.
Auxiliary System Equipment - The control cabinets for auxiliary systems, such as fire alarm, etc., shall be identified with nameplate describing the system by designation, power circuit voltage.


E.
Junction and Pull Boxes - Identify the function of the box, such as "208 volt", "telephone", "fire alarm", etc. with labels.


F.
Fusible Switches - In addition to the nameplate, there shall be labeled on the inside of switch door, the fuse size required for equipment served.

3.3
RACEWAY IDENTIFICATION


A.
In general, all exposed feeder conduits, wire ways, etc., shall be identified.  Branch circuit conduits from panelboards to load need not be identified.


B.
The identification labels shall be located at intervals of 50 feet or less and at every point where a conduit or raceway is entering and leaving a room.


C.
All emergency power conduit, fire alarm conduit and junction boxes shall be spray painted, red, every 8 feet (approximately).

3.4
CONDUCTOR IDENTIFICATION


A.
All conductors in junction boxes shall be identified and labeled with panel and circuit number designation.


B.
All telephone cables shall be identified at each end with matching labels and department.  Record drawing shall be provided to Owner's field representative.

3.5
RESPONSIBILITY


A.
Identification nameplates and labels shall be provided for all equipment and raceways installed under this Contract or as indicated on drawings.  It shall include all equipment, such as motor starters and boxes furnished by others.

END OF SECTION

EQUIPMENT AND CONDUIT IDENTIFICATION
16019-2

