Mr. Kirk Pichon

City of Slidell

2055 Second Street

Slidell, Louisiana  70458

RE:
2585 Front Street

Dear Mr. Pichon,

The following is in response to your letter dated January 28, 2005, copy attached:

BUILDING

1) Although the State Fire Marshal’s office has waived the accessibility requirement based on a letter from Textron the building would still have to meet the requirements of section 3408 of the IBC.  Plans shall be resubmitted to reflect these changes.

A.  Plans are revised to show handicap facilities in the office area only.
2) I’m not sure how we are getting a one-hour floor ceiling assembly over the lunch room area when it is entirely within the factory area and surrounded by three house walls

A. The three-hour wall and one-hour floor assembly will be removed from the lunch room walls.  A three house firewall shall be installed on the south wall of the warehouse.
3) Uplift connection notes sheet A-4 should be for 130 mph.

A.  Has been revised to 130 mph.
MECHANICAL

1) Bathroom exhaust shall be at a rate of 75 cfm per water closet or urinal Table 403.3.

A.  Drawings have been revised.
2) 405.1 General.

A.  Contractor shall demonstrate.
3) 606.2.1 Return air systems.

A.  Drawings have been revised.
4) 606.4.1 Supervision.

A.  Contractor shall follow.
5) An air balance report shall be provided prior to final inspection to verify compliance with Chapter 4.

A.  Contractor shall comply.
6) Please supply calculations for ventilation air in dining room only.

A.  See revised schedule.
7) Access to unit in attic space shall comply with section 306.3.

A.  Each A/C unit shall have pull-down stairs access
PLUMBING

No Comments

ELECTRICAL

No Comments

If you have any questions, or require any further information, please call.

Sincerely,

Chuck Dammon

