Answer to items e-mailed 11-31-08.

#1 Change size on plan for conductors from generator to building to read.

2( 6-750 MCM, 1-4/0 N, 1-3/0 GRD, 5” C)

1( 5” spare conduit)

This will allow full capacity of generator to be used, if ever needed, the odd number of conductors was a typo.

#2 The feed from transfer switch to 600A MDP is:

1-(6-400MCM, 1-400MCM N, 1-3/0 GRD, 5” sch 80 PVC C

#3 Feed from transfer switch to the new 1200A fused safety switch, and from the new 1200A fused safety switch to the existing 1200A MDP, Change to read. 2(3-700 MCM,1-700MCM N, 1-3/0 GRD, 5” C)
Generator Note:

1. All exterior conductors shall be type THWN

2. All interior conductors shall be type THHN

