Textron Marine & Land 

252 Stone Road

Slidell, La. 70460

New 1000kw Generator

Addendum #1

Meeting notes from Textron Marine

1) There is no bonding requirement for this project. The contractor shall supply with his   bid a copy of insurance. 

2) There are guards on duty 24/7 and will not require a fire watchman.

3) Contractor shall remove the existing conduit and wire from the firehouse to the bldg.

& Install new as indicated. See dwg E-1.

4) Contractor shall install control circuit from the transfer switch to the generator. See dwg E-1.

5) Relocate the existing transformer that is located inside the bldg. to the Isle as noted on the dwg. See dwg E-1.

6) When will the generator be on site for installation?

Owner shall coordinate with contractor and generator vendor to have unit on site when required.
7) Bids are due on November 3rd. All bids shall be turned into 

    Textron Marine & Land

    Teresa Bergeron

    19401 Chef Menteur Hwy

    New Orleans, La. 70129-2577

    Fax# 504-254-6317

    Cell# 504-270-7295 

8) Shut down shall be between the hours of 2am Friday and 4:30 am Monday morning.

9) The fire pump is not required to have its own transfer switch.

10) The foundation shall be grounded to the generator.

      See the attached E-1 dwg.

11) Contractor shall provide all required lifting equipment to install new 1000kw   generator. 

