DAMMON ENGINEERING, INC.

dammonengineering.com


CONSULTING

DESIGN

STUDIES

EXPERT WITNESS


1095 Florida Ave.



   P.O. Box 2830



     985-649-5832

Slidell, LA 70458



Slidell, LA  70459


            FAX 985-641-5950

November 3, 2008

Textron Marine & Land 

252 Stone Road

Slidell, La. 70460

New 1000kw Generator

Addendum #2

See the attached One Line Diagram.

1) Change size on plan for conductors from generator to building to read.

   (6-750 MCM, 1-4/0 N, 1-3/0 GRD, 5” C)

   1(5” spare conduit)

  This will allow full capacity of the generator to be used, if ever needed; the odd number of conductors was a

   typo.

2) The feed from transfer switch to 600A MDP is:

   1-(6-400MCM, 1-400MCM N, 1-3/0 GRD, 5” schedule 80 PVC C

3) Feed from transfer switch to the new 1200A fused safety switch, and from the new 1200A fused safety switch

    to the existing 1200A MDP, Change to read. 2(3-700 MCM, 1-700MCM N, 1-3/0 GRD, 5” C)

4) A. All exterior conductors shall be type THWN.

    B. All interior conductors shall be type THHN.

The bid date has been extended by one day. The new due date is 11-06-08.

Chuck Dammon 

Dammon Engineering
