[image: image1.jpg]IDAMMON

ENGINEERING | NLC.

J  Archiltectls & Engineers




554 Old Spanish Trail
Slidell, LA 70458

Phone: 985-649-5832

Fax: 985-641-5950

dammonengineering.com

dammoneng@bellsouth.net


April 19, 2013
Mr. Anouar Ait Iddir

Senior Building Plan Reviewer

City of New Orleans

Dept. of Safety & Permits

1300 Perdido Street, Suite 7E06

New Orleans, LA 70112

RE:
Permit No. 12-09985-RNVN


19401 Chef Menteur Hwy


(Textron Marine &Land Systems), Bldg #3

Dear Mr. Iddir,

We are in receipt of your review letter dated April 09, 2013 and offer the following responses.

Architectural:

2.
Doors shall swing in the direction of egress travel where serving an occupant load of 50 or more in accordance with section 1008.1.2 of IBC 2009.  Ref: Exit Staircase next to office 205.


The building is existing, non-conforming & is less than 50% whole building renovation.

Electrical:

1. Please note all wiring shall be as per NEC 2011 edition.

All wiring shall be as per NEC 2011 edition.
2.
Sheet E1 and E2, a 125-volt, single-phase, 15 or 20 ampere-rated GFCI protected receptacle outlet shall be provided for the serving of ALL New A/C Condenser Units as per NEC 2011 Art. 210.63 and 210.8. Please verify.


Please see sheet E1, E2 for location.  These shall be GFCI protected.
3.
Sheet E5, please provide the calculated available maximum shorted circuit current from the utility company for ALL New Panels.  We need these values to compare and confirm with NEC 2011 Art. 110.9, 240.12, 225.53, 230.82(3), 230.205(B), 240.92(C) (1) and 230.208.

Please see attached.
Mechanical:

1. Your mechanical (hvac) floor plans as submitted do not indicate location of fire dampers and fire damper classifications/specification, which are required for our review.

There are no fire walls in this project.  The only firewalls are between buildings & stairwells.  We have no ductwork penetrations.
2. Your mechanical floor plans do not indication locations of O/A complete with louvers/screen.  Please indicate on the plans for clarity.

Please see sheets M1 & M2 for locations of O/A.  See sheet A6 for locations and type.
3. Your mechanical plans do not indicate locations and installations details for air handlers meeting requirements per all applicable sections/subsections, Chapter 3, IMC 2009.

Please see sheets M1 & M2 for AHU locations.  See sheet M3 for ceiling mounted AHU & Ductwork details.
4. Your Mechanical plans do not indicate duct support details complete with insulations meeting requirements per applicable sections, Chapter 6, IMC 2009.

Please see sheet M3 for details & HVAC notes.

If you have any questions, or require any additional information, please feel free to call.


Please mail all correspondence to:

Dammon Engineering, Inc.









554 Old Spanish Trail









Slidell, LA 70458

Sincerely,

Kevin J. Kinchen, Chief Architect

Dammon Engineering, Inc.
Bill Kingsmill’s contact information is as follows:
William Kingsmill (kingsmillprop@bellsouth.net)
Cell: (504) 528 3838
1200 Business Highway 190, Suite 13
Covington, LA 70433
 
Lawrence Wm. Haik, Sr
Republic Commercial Properties, LLC                
1539 Royal Palm Dr.
Slidell, LA 70458
(985) 960-7033
 
