[image: image1.jpg]


554 Old Spanish Trail

Slidell, LA 70458

Phone: 985-649-5832

Fax: 985-641-5950

dammonengineering.com

info@dammonengineering.com

September 4, 2015
Mr. Richard Ledet

Director, Operational Excellence

Textron Marine & Land Systems 

An Operating Unit of Textron Marine 

1010 Gause Blvd. 
Slidell, LA 70458

RE:
Shipyard Facilities Operation


19401 Chef Menteur Hwy 



New Orleans, La.

Dear Mr. Ledet,

Dammon Engineering visited the shipyard on 9/3/15 and walked the site with Pat Pendergraft to determine the possibilities of additional manufacturing buildings per the attached sketch.

Building #2:
The north side of building #2 would allow for expansion. The new expansion would be a lean-to type to be attached to the highest eve height allowed of the existing building and the full depth of building #2.

There are numerous objects in the way of this addition: electrical, sewage, mechanical devices for the doors on building #2 and platforms.  All these items can be relocated and still allow for the existing road on the north side.  It was mentioned to us that there are existing pilings in the ground for future expansion.  It would be helpful to locate these drawings. 

Building #5:
The south side of building #5 would allow for expansion. The new expansion would attach to building #5 and go south as noted on the attached sketch. 
There are numerous objects in the way of this addition: the main sewage treatment plant for this facility, site drainage, potable water and electrical. All these items can be relocated.

Existing boat slip:
The existing boat slip is encompassed in sheet piles (steel bulkhead) and the average depth is 5 to 8 feet. There are several discharges (sewage and site drainage) into this boat slip that can be relocated to allow the expansion of building #5.  A new bulkhead can be installed to close this area off and fill the void with new fill. 

If you have any questions, or require additional information, please feel free to call.

Sincerely,

[image: image2.png]



David Dammon, VP
Dammon Engineering, Inc.

Attachments:
Chef Hwy Site Plan




Pictures: 2544, 2549, 2487, 2496

xc:
Mr. Daniel Latournerie

