Dammon Engineering, Inc.

dammonengineering.com


1095 Florida Ave.



P.O. Box 2830



            985-649-5832

Slidell, LA 70458



Slidell, LA  70459


   FAX 985-641-5950

May 17, 2006

Mr. Greg Gardiol

NY Associates Inc.

For Jefferson Parish Inspection & Code Enforcement

2750 Lake Villa Dr.

Metairie, LA 70002-0595

RE:  
Job No: CE-129058-06


Location : 3838 N. Causeway Boulevard

Dear Mr. Gardiol,

The following is in response is to your letter dated May 4, 2006:  

1. Riser Diagram has been revised please see plumbing plan attached.

2. See revised plumbing plan attached.

3. See revised plumbing plan attached.

4. Shower waste and vent connections have been revised to 2”.  See revised plumbing plan attached.

5. See revised plumbing plan attached.

6. Break room refrigerator does not require domestic cold water for ice maker.  A separate ice maker is going to be installed.  See revised plumbing plan attached.

7. See revised plumbing plan attached.

8. Home Run circuit breaker numbers have not been identified, they are currently being used in this suite.  Existing circuit breakers will be re-used according electrical note number 1.  Electrician will identify in the field which breakers are to be re-used

9. Note #2 was a typographical error, a hold over from a previous project electrical notes.  No additional power panels will be required for this project on this floor.

10. Egress has not been changed for this project on this floor.  

11. Existing Emergency Lights are to be re-used.

12. Note #15 was a typographical error to include NMC on this project.  It has been removed.  See revised electrical plan.

13. Existing panels will support this project.  Existing breakers will be re-used.  No additional load will be added by this project.

14. A reflected ceiling plan is attached.

Sincerely,

David Dammon

Project Manager

