## Fixture Schedule
LIGHTING FIXTURE SCHEDULE
FIXTURE TYPE | MANUFACTURER | CATALOG # | WATTAGE
F1 | HUBBELL | CCL24-5035 | 44 WATTS
F1E | HUBBELL | CCL24-5035-ELL14 | 44 WATTS
F2 | HUBBELL | CCL22-3335 | 29 WATTS
F2E | HUBBELL | CCL22-3335-ELL14 | 29 WATTS
F3 | LITON | CH618UE-D10/CR6L22SW-T35 | 18 WATTS
F3E | LITON | CH618UE-D10-EM/CR6L22SW-EMA-T35 | 18 WATTS
F3A | LITON | CH618UE-D10/CR6L22SW-T35 | 18 WATTS
F3AE | LITON | CH618UE-D10-EM/CR6L22SW-EMA-T35 | 18 WATTS
F4 | BROWNLEE | 5160-24-BN-H13-EC1-35K | 13 WATTS
F5 | BROAN | 678 | 100 WATTS
F6 | HUBBELL | SG1-40-4K7-FT-UNV-DB | 38 WATTS
EX | COMPASS | CER | 1 WATT

## RISER
M
|  |  |  | ② | 250V 3P 200A N-3R |  | PANEL "LP"
| 120/208 3P 4W |  |  |  |  | ③ | (SEE SCHEDULE)
| 200A |  |  |  | FDS S.E. RATED
GROUND PER NEC
①
ONE-LINE DIAGRAM
| ① | COORDINATE CONDUIT SIZE AND QUANTITY WITH POWER CO.
| ② | 4 - 3/0 MCM THHN AND 1#6 GROUND IN 2" CONDUIT
| ③ | 4 - 3/0 MCM THHN AND 1#6 GROUND IN 2" CONDUIT

## PANEL LP
PANEL "LP"
120/208 3P 4W 200A MLO N-1 FLUSH MOUNT
| Description |  | Volt | Volt | Volt |  |  | Volt | Volt | Volt |  | Description
Circuit |  | Conductor | Amps | Amps | Amps | Breaker | Breaker | Amps | Amps | Amps | Conductor |  | Circuit
No. |  | Size | A | B | C | Size | Size | A | B | C | Size |  | No.
1 | RECEPTACLES | #12 | 800 |  |  | 1P 20A | 1P 20A | 600 |  |  | #12 | RECEPTACLES | 2
3 | RECEPTACLES | #12 |  | 800 |  | 1P 20A | 1P 20A |  | 800 |  | #12 | RECEPTACLES | 4
5 | RECEPTACLES | #12 |  |  | 1000 | 1P 20A | 1P 20A |  |  | 1000 | #12 | RECEPTACLES | 6
7 | RECEPTACLES | #12 | 1000 |  |  | 1P 20A | 1P 20A | 800 |  |  | #12 | RECEPTACLES | 8
9 | RECEPTACLES | #12 |  | 1750 |  | 1P 20A | 1P 20A |  | 1750 |  | #12 | RECEPTACLES | 10
11 | RECEPTACLES | #12 |  |  | 1750 | 1P 20A | 1P 20A |  |  | 600 | #12 | RECEPTACLES | 12
13 | RECEPTACLES | #12 | 600 |  |  | 1P 20A | 1P 20A | 600 |  |  | #12 | RECEPTACLES | 14
15 | RECEPTACLES | #12 |  | 600 |  | 1P 20A | 1P 20A |  | 1750 |  | #12 | REFRIGERTAOR | 16
17 | RECEPTACLES | #12 |  |  | 1750 | 1P 20A | 1P 20A |  |  | 1750 | #12 | RECEPTACLES | 18
19 | RECEPTACLES | #12 | 1000 |  |  | 1P 20A | 1P 20A | 708 |  |  | #12 | LIGHTING | 20
21 | LIGHTING | #12 |  | 1141 |  | 1P 20A | 1P 20A |  | 300 |  | #12 | LIGHTING | 22
23 | WATER HEATER | #10 |  |  | 2880 | 1P 30A | [5 empty] | SPACE | 24
25 | AHU-1 | #8 | 3910 |  |  | 3P 40A | 3P 40A | 3910 |  |  | #8 | AHU-2 | 26
27 |  |  |  | 3910 |  |  |  |  | 3910 |  |  |  | 28
29 |  |  |  |  | 3910 |  |  |  |  | 3910 |  |  | 30
31 | CU-1 | #10 | 2400 |  |  | 3P30A | 3P 30A | 2400 |  |  | #10 | CU-2 | 32
33 |  |  |  | 2400 |  |  |  |  | 2400 |  |  |  | 34
35 |  |  |  |  | 2400 |  |  |  |  | 2400 |  |  | 36
37 | [12 empty] | 38
39 | [12 empty] | 40
41 | [12 empty] | 42
|  | Phase | 7310 | 8201 | 11290 |  | Phase | 6618 | 8510 | 7260
[7 empty] | Phase Tot. | 13928 | 16711 | 18550
[7 empty] | Total VA | 49189
SPECIFIC NOTES
① | PROVIDE 250V 3P 60A N-1 FDS, FUSE PER MANUFACTURERS RECOMMENDATIONS
② | PROVIDE 250V 3P 30A N-3R FDS, FUSE PER MANUFACTURERS RECOMMENDATIONS