Dammon Engineering, Inc.

dammonengineering.com


1095 Florida Ave.



P.O. Box 2830



            985-649-5832

Slidell, LA 70458



Slidell, LA  70459


   FAX 985-641-5950

December 1, 2010

Mr. Dean Born

LA IBTS

RE:  
MARCO'S PIZZA SELA#1

2349 EAST GAUSE BLVD

SUITE 1

SLIDELL, LA  70469

Dear Mr. Born,

With regard to the above referenced project, the existing demising wall between Suite 1 and Suite 2 was incorrectly labeled on our construction drawings.  The construction drawings showed this existing demising wall as an existing 2-hr rated wall.  This wall should have been labeled as existing 1-hr. rated wall.  Please see attached drawing.

The current tenant in Suite #2 is a Smoothie King restaurant, also the owner of the building; Smoothie King has the same square footage as the new Marco’s Pizza, 1200 s.f.  Both Smoothie King and Marco’s Pizza would be the same occupancy, Assembly under 50 occupants – Business.  According to IBC 2006, table 508.3.3, there is no separation required between the same occupancies.  Therefore a 1-hr. rated wall complies with the IBC 2006.

Instructions have been provided to the contractor to maintain the existing 1-hr fire rating.

If you have any questions, please feel free to call.

Sincerely,

David Dammon

Project Manager

