Chuck,

Entries in Panel Schedule

CIRCUIT	WIRE SIZE	LOAD	AMP	POLE	LOAD VA

14	#10	MINI SPLIT,  VESTIBULE	20	2	1285

12						1285

10	#12	DOOR OPENERS, VESTIBULE	20	1	756

8	#12	LIGHTING AND OUTDOOR GFI RECEPT,	20	1	583

VESTIBULE

I noticed your drawing says to use EMT conduit.  As far as the conduit and wire go, you have two options:

One Conduit:

¾”C,4 #12 (2 HOT, 2 N) 3 #10 (2 HOT, 1 GND)

Two Conduits:

¾”C, 5 #12 (2 HOT, 2 N, 1 GND)

¾”C, 3 #10 (2 HOT, 1 GND)