ST. TAMMANY PARISH SCHOOL BOARD

PEARL RIVER HIGH SCHOOL

SOCCER FIELD LIGHTING
PEARL RIVER LA


Copyright 2011 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 260526
GROUNDING AND BONDING FOR ELECTRICAL SYSTEMS
Revise this Section by deleting and inserting text to meet Project-specific requirements.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

NFPA 70 and IEEE C2 include basic grounding requirements for electrical safety. This Section supplements those requirements with additional grounding requirements and with optional grounding methods and materials for both power and electronic systems that go beyond basic minimum safety requirements.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section includes grounding and bonding systems and equipment.

1.2 ACTION SUBMITTALS

A. Product Data: For each type of product indicated.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 MANUFACTURERS

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

A. Manufacturers: Available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following:

Retain "Basis-of-Design Product" Paragraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

1. Burndy; Part of Hubbell Electrical Systems.

2. Dossert; AFL Telecommunications LLC.

3. ERICO International Corporation.

4. Fushi Copperweld Inc.

5. Galvan Industries, Inc.; Electrical Products Division, LLC.

6. Harger Lightning and Grounding.

7. ILSCO.

8. O-Z/Gedney; A Brand of the EGS Electrical Group.

9. Robbins Lightning, Inc.

10. Siemens Power Transmission & Distribution, Inc.

2.2 SYSTEM DESCRIPTION

A. Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

B. Comply with UL 467 for grounding and bonding materials and equipment.

2.3 CONDUCTORS

Retain "Insulated Conductors" Paragraph below to require one of the two preferred conductor materials permitted by NFPA 70; delete to allow Contractor to use any material that complies with Code. See "Grounding Products" Article in the Evaluations for discussion on alternative materials.

A. Insulated Conductors: Copper or tinned-copper wire or cable insulated for 600 V unless otherwise required by applicable Code or authorities having jurisdiction.

B. Bare Copper Conductors:

1. Solid Conductors: ASTM B 3.

2. Stranded Conductors: ASTM B 8.

3. Tinned Conductors: ASTM B 33.

Sizes and types of conductors in four subparagraphs below are typical examples. 28-kcmil bonding cable in "Bonding Cable" Subparagraph below is slightly larger than No. 6 AWG.

4. Bonding Cable: 28 kcmil, 14 strands of No. 17 AWG conductor, 1/4 inch  in diameter.

5. Bonding Conductor: No. 4 or No. 6 AWG, stranded conductor.

6. Bonding Jumper: Copper tape, braided conductors terminated with copper ferrules; 1-5/8 inches  wide and 1/16 inch  thick.

7. Tinned Bonding Jumper: Tinned-copper tape, braided conductors terminated with copper ferrules; 1-5/8 inches  wide and 1/16 inch  thick.

2.4 CONNECTORS

A. Listed and labeled by an NRTL acceptable to authorities having jurisdiction for applications in which used and for specific types, sizes, and combinations of conductors and other items connected.

B. Bolted Connectors for Conductors and Pipes: Copper or copper alloy.

C. Welded Connectors: Exothermic-welding kits of types recommended by kit manufacturer for materials being joined and installation conditions.

D. Bus-Bar Connectors: Mechanical type, cast silicon bronze, solderless compression or exothermic-type wire terminals, and long-barrel, two-bolt connection to ground bus bar.

2.5 GROUNDING ELECTRODES

Grounding electrodes include ground rods, metal underground water pipes, metal building frames, concrete-encased electrodes, and pipe and plate electrodes. Retain "Applications" and "Installation" articles to specify where these items are required; coordinate with Drawings.

Copper-clad steel ground rods are the most common grounding electrode. See Evaluations for discussion on alternative materials. Sectional rods are used when electrodes longer than 10 feet (3 m) are required.

A. Ground Rods: Copper-clad steel 5/8 by 96 inches.

PART 3 -  EXECUTION

3.1 APPLICATIONS

A. Conductors: Install solid conductor for No. 12 AWG and smaller, and stranded conductors for No. 12 AWG and larger unless otherwise indicated.

Coordinate "Underground Grounding Conductors" Paragraph below with Drawings and with Section 260543 "Underground Ducts and Raceways for Electrical Systems."

B. Conductor Terminations and Connections:

1. Pipe and Equipment Grounding Conductor Terminations: Bolted connectors.

2. Underground Connections: Welded connectors except at test wells and as otherwise indicated.

3. Connections to Ground Rods at Test Wells: Bolted connectors.

4. Connections to Structural Steel: Welded connectors.

3.2 GROUNDING AT THE SERVICE

A. Equipment grounding conductors and grounding electrode conductors shall be connected to the ground bus. Install a main bonding jumper between the neutral and ground buses.

3.3 EQUIPMENT GROUNDING

NFPA 70 permits two types of equipment grounding conductors: metallic raceway or cable sheath that encloses supply conductors, and a separate grounding conductor of insulated wire or cable installed with supply conductors. Installation of a separate insulated equipment grounding conductor provides an additional degree of safe operation when compared to relying on raceway or cable sheath for ground continuity. NFPA 70 requires separate insulated equipment grounding conductors in some situations and not in others. Retain and revise one of first two paragraphs below to require insulated equipment grounding conductors that exceed NFPA 70 requirements. Coordinate with Drawings.

A. Install insulated equipment grounding conductors with all feeders and branch circuits.

B. Install insulated equipment grounding conductors with the following items, in addition to those required by NFPA 70:

Retain applicable subparagraphs below.

1. Feeders and branch circuits.

2. Lighting circuits.

3. Receptacle circuits.

3.4 INSTALLATION

A. Grounding Conductors: Route along shortest and straightest paths possible unless otherwise indicated or required by Code. Avoid obstructing access or placing conductors where they may be subjected to strain, impact, or damage.

B. Ground Bonding Common with Lightning Protection System: Comply with NFPA 780 and UL 96 when interconnecting with lightning protection system. Bond electrical power system ground directly to lightning protection system grounding conductor at closest point to electrical service grounding electrode. Use bonding conductor sized same as system grounding electrode conductor, and install in conduit.

C. Bonding Straps and Jumpers: Install in locations accessible for inspection and maintenance except where routed through short lengths of conduit.

1. Bonding to Structure: Bond straps directly to basic structure, taking care not to penetrate any adjacent parts.

2. Bonding to Equipment Mounted on Vibration Isolation Hangers and Supports: Install bonding so vibration is not transmitted to rigidly mounted equipment.

3. Use exothermic-welded connectors for outdoor locations; if a disconnect-type connection is required, use a bolted clamp.

If connections specified in "Grounding and Bonding for Piping" Paragraph below circumvent dielectric fittings intended to isolate interior piping systems from ground, other action may be necessary to prevent electrolytic corrosion.

3.5 FIELD QUALITY CONTROL

A. Perform tests and inspections. Inspect physical and mechanical condition. Verify tightness of accessible, bolted, electrical connections with a calibrated torque wrench according to manufacturer's written instructions.

END OF SECTION 260526

	GROUNDING AND BONDING FOR ELECTRICAL SYSTEMS
	260526 - 3



