ST. TAMMANY PARISH SCHOOL BOARD

PEARL RIVER HIGH SCHOOL

SOCCER FIELD LIGHTING
PEARL RIVER LA


Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 260533
RACEWAYS AND BOXES FOR ELECTRICAL SYSTEMS
Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

PART 1 -  GENERAL

1.1 SUMMARY

A. Section Includes:

1. Metal conduits, tubing, and fittings.

2. Boxes, enclosures, and cabinets.

PART 2 -  PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

2.1 METAL CONDUITS, TUBING, AND FITTINGS

A. Listing and Labeling: Metal conduits, tubing, and fittings shall be listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

B. GRC: Comply with ANSI C80.1 and UL 6.

Retain "ARC" Paragraph below for corrosion resistance and for power distribution at frequencies above 60 Hz or for other special conditions.

C. ARC: Comply with ANSI C80.5 and UL 6A.

D. IMC: Comply with ANSI C80.6 and UL 1242.

E. EMT: Comply with ANSI C80.3 and UL 797.

In "FMC" Paragraph below, zinc-coated steel is most common type and provides some additional protection from physical damage. Aluminum is much lighter and easier to install.

F. LFMC: Flexible steel conduit with PVC jacket and complying with UL 360.

G. Fittings for Metal Conduit: Comply with NEMA FB 1 and UL 514B.

Coordinate "Conduit Fittings for Hazardous (Classified) Locations" Subparagraph below with Drawings.

1. Conduit Fittings for Hazardous (Classified) Locations: Comply with UL 886 and NFPA 70.

2. Fittings for EMT:

a. Material: Steel or die cast.

b. Type: Setscrew or compression.

3. Expansion Fittings: PVC or steel to match conduit type, complying with UL 651, rated for environmental conditions where installed, and including flexible external bonding jumper.

4. Coating for Fittings for PVC-Coated Conduit: Minimum thickness of 0.040 inch, with overlapping sleeves protecting threaded joints.

Retain "Joint Compound for IMC, GRC, or ARC" Paragraph below to require some threaded joints of IMC, GRC, ARC, or their fittings, to be treated with joint compound for improved conductivity, resistance to oxidation, or ease of assembly and disassembly.

H. Joint Compound for IMC, GRC, or ARC: Approved, as defined in NFPA 70, by authorities having jurisdiction for use in conduit assemblies, and compounded for use to lubricate and protect threaded conduit joints from corrosion and to enhance their conductivity.

PART 3 -  EXECUTION

3.1 RACEWAY APPLICATION

Retain this article to specify type of raceway to be installed. Coordinate with conductor and cable wiring methods specified in Section 260519 "Low-Voltage Electrical Power Conductors and Cables" and in other electrical, communications, and security Sections. See "Writing Guide" Article in the Evaluations for instructions on editing this article.

A. Minimum Raceway Size: 1/2-inch trade size.

B. Raceway Fittings: Compatible with raceways and suitable for use and location.

1. PVC Externally Coated, Rigid Steel Conduits: Use only fittings listed for use with this type of conduit. Patch and seal all joints, nicks, and scrapes in PVC coating after installing conduits and fittings. Use sealant recommended by fitting manufacturer and apply in thickness and number of coats recommended by manufacturer.

2. EMT: Use setscrew or compression, steel or cast-metal fittings. Comply with NEMA FB 2.10.

3. Flexible Conduit: Use only fittings listed for use with flexible conduit. Comply with NEMA FB 2.20.

C. Do not install aluminum conduits, boxes, or fittings in contact with concrete or earth.

Coordinate first paragraph below with Drawings.

3.2 INSTALLATION

A. Comply with NECA 1 and NECA 101 for installation requirements except where requirements on Drawings or in this article are stricter. Comply with NECA 102 for aluminum conduits. Comply with NFPA 70 limitations for types of raceways allowed in specific occupancies and number of floors.

B. Keep raceways at least 6 inches away from parallel runs of flues and steam or hot-water pipes. Install horizontal raceway runs above water and steam piping.

C. Comply with requirements in Section 260529 "Hangers and Supports for Electrical Systems" for hangers and supports.

D. Arrange stub-ups so curved portions of bends are not visible above finished slab.

First paragraph below is more restrictive than NFPA 70, which permits up to four quarter bends in a conduit run. Retain paragraph for more conservative design, with less stress being placed on conductors being pulled in.

E. Install no more than the equivalent of three 90-degree bends in any conduit run except for control wiring conduits, for which fewer bends are allowed. Support within 12 inches of changes in direction.

F. Conceal conduit and EMT within finished walls, ceilings, and floors unless otherwise indicated. Install conduits parallel or perpendicular to building lines.

G. Support conduit within 12 inches of enclosures to which attached.

Retain "Threaded Conduit Joints, Exposed to Wet, Damp, Corrosive, or Outdoor Conditions" Paragraph below to require application of protective joint compound to threads of rigid steel conduit or IMC and to their fittings where these raceways are installed outdoors or in wet, damp, or corrosive conditions. This optional requirement exceeds NFPA 70 rules. If retaining, coordinate with Drawings indicating wet, damp, or corrosive indoor locations.

H. Threaded Conduit Joints, Exposed to Wet, Damp, Corrosive, or Outdoor Conditions: Apply listed compound to threads of raceway and fittings before making up joints. Follow compound manufacturer's written instructions.

Retain one of first two paragraphs below to exceed NFPA 70 requirements. NFPA 70 requires insulated bushings or other smooth, rounded entry provisions for conduit terminations at all locations where conductors are No. 4 AWG and larger, regardless of the environment. NFPA 70 requires bonding of all service conductors, but does not require bonding to be accomplished with grounding bushings. See Evaluations for further discussion.

I. Raceway Terminations at Locations Subject to Moisture or Vibration: Use insulating bushings to protect conductors including conductors smaller than No. 4 AWG.

J. Terminate threaded conduits into threaded hubs or with locknuts on inside and outside of boxes or cabinets. Install bushings on conduits up to 1-1/4-inch trade size and insulated throat metal bushings on 1-1/2-inch trade size and larger conduits terminated with locknuts. Install insulated throat metal grounding bushings on service conduits.

K. Install pull wires in empty raceways. Use polypropylene or monofilament plastic line with not less than 200-lb tensile strength. Leave at least 12 inches of slack at each end of pull wire. Cap underground raceways designated as spare above grade alongside raceways in use.

Retain "Surface Raceways" Paragraph below if applicable.

L. Install raceway sealing fittings at accessible locations according to NFPA 70 and fill them with listed sealing compound. For concealed raceways, install each fitting in a flush steel box with a blank cover plate having a finish similar to that of adjacent plates or surfaces.

See Evaluations for discussion of types of and locations for raceway seals.

M. Install devices to seal raceway interiors at accessible locations. Locate seals so no fittings or boxes are between the seal and the following changes of environments. Seal the interior of all raceways at the following points:

1. Where conduits pass from warm to cold locations, such as boundaries of refrigerated spaces.

2. Where an underground service raceway enters a building or structure.

3. Where otherwise required by NFPA 70.

Retain "Expansion-Joint Fittings" Paragraph below unless locations for expansion fittings for RNC are indicated on Drawings. See Evaluations.

N. Expansion-Joint Fittings:

1. Install type and quantity of fittings that accommodate temperature change listed for each of the following locations:

Revise list below to include all locations in Project with environmental conditions that require considering expansion-joint fittings in conduit runs. For each Project, consider only locations with PVC conduit with straight-run length exceeding 25 feet (7.6 m). Also revise temperature change for each location so it safely represents conditions anticipated. Temperature-change figures below are examples of maximum total swings from the lowest to the highest environmental temperatures at the indicated types of locations and must be revised to represent temperature swings or changes that may occur at Project locations.

a. Attics: 135 deg F temperature change.

Formula in first subparagraph below provides about 15 percent safety factor (extra expansion-contraction capability).

2. Install expansion fittings at all locations where conduits cross building or structure expansion joints.

3. Install each expansion-joint fitting with position, mounting, and piston setting selected according to manufacturer's written instructions for conditions at specific location at time of installation. Install conduit supports to allow for expansion movement.

Retain option in "Flexible Conduit Connections" Paragraph below if flexible connections are required for recessed and semirecessed luminaires.

O. Flexible Conduit Connections: Comply with NEMA RV 3. Use a maximum of 72 inches of flexible conduit for recessed and semirecessed luminaires, equipment subject to vibration, noise transmission, or movement; and for transformers and motors.

1. Use LFMC in damp or wet locations subject to severe physical damage.

2. Use LFMC or LFNC in damp or wet locations not subject to severe physical damage.

P. Fasten junction and pull boxes to or support from building structure. Do not support boxes by conduits.

3.3 SLEEVE AND SLEEVE-SEAL INSTALLATION FOR ELECTRICAL PENETRATIONS

A. Install sleeves and sleeve seals at penetrations of exterior floor and wall assemblies. Comply with requirements in Section 260544 "Sleeves and Sleeve Seals for Electrical Raceways and Cabling."

3.4 PROTECTION

A. Protect coatings, finishes, and cabinets from damage and deterioration.

1. Repair damage to galvanized finishes with zinc-rich paint recommended by manufacturer.

2. Repair damage to PVC coatings or paint finishes with matching touchup coating recommended by manufacturer.

END OF SECTION 260533

	RACEWAYS AND BOXES FOR ELECTRICAL SYSTEMS
	260533 - 1



