January 10, 2003

Mr. Keith Pumilia

Pumilia Contractors, Inc.

1120 Hancock St.

Gretna, Louisiana  70053

RE:
59 Maintenance Barn

Dear Keith,

Please note the following:

1.
We have reduced the size of the treatment plant from 2,000 gallon chlorinated with effluent reduction system to 1,000 gallon chlorinated with effluent reduction system. These are shown on DWG C-1 & M-1.
2.
The auto transfer switch has been increased from 150 amp, 250 volt 3 pole, To a 400 amp, 250 volt 3 pole. This is shown on DWG. E-2.

3.
Lightning protection shall have copper wire in ground up to 5’ high the remainder shall be aluminum as shown on Sheet E-3.

These changes are reflected on the updated drawings given to you with this information.

Please call to let me know that you received this.  If you have any questions, or require any further information, please feel free to call.

Sincerely,

Chuck Dammon/Project Manager

Dammon Engineering, Inc.

