April 8, 2002

Ms Cynthia Obier

State of Louisiana

Department of Public Safety and Corrections

Office of State Fire Marshal/Code Enforcement and Building Safety.

5150 Florida Blvd.

Baton Rouge, Louisiana 70806

RE:
Camellia Gardens

P0233508

Dear Ms. Obier

Per our telephone conversation on 4-4-02, we are resubmitting the drawings for approval as a Residential Board and Care Occupancy. This letter, in addition to the enclosed information from Mark Development, is to clarify the type of building we have designed and what is actually being constructed on the site. 

There are a total of six buildings for this project. Three of the six buildings are two stories; two of these have Assisted Living Services on the second floors; the first floors of the two buildings have Independent Living services. The other three buildings are Single Story and have Independent Living Services, one of which has a kitchen and dining room.

We originally designed the rooms to have firewalls extending to the underside of the roof. The contractor has opted to encapsulate the rooms by having two layers of 5/8” type “X” sheet rock on the ceiling and one layer of 5/8” type “X” on the walls. All corridor halls are also encapsulated. The two story buildings have a layer of ¾” Gypsum Crete with ¾” plywood as the floor surface of the second floor.

All corridors and apartments are sprinkled. Two of the buildings are sprinkled in the attics that have assembly areas. All corridors and apartments have smoke and fire detection and alarm. All apartments have nurse calls.

Please call me with any questions that you may have.  We appreciate your help with this matter.

Thank you,

Chuck Dammon

VP/Project Manager
