La Quanta Inns & Suites New Orleans downtown

Answers to city of New Orleans comments

B-99006427

1. OK

2. VOID

3. OK

4. UL Listing is not voided by tapping bus of MCC using tap rule.

5. MCCA will have a main disconnect with normal 200 AMP fuses, rated 200 000 A.I.C.

Sincerely,

Emmett G (Pete) Dammon P.E.,

plc/EGD

