July 12, 2000

Buddy Domingue

Office of the State Fire Marshall

5150 Florida Ave

Baton Rouge, LA 70806

RE;
P0171391 Pelican Pointe Apartments, Slidell, LA

Dear Buddy;

  Attached please find copies of previous correspondence on the Pelican Pointe project, with regards to electrical drawings.  Also my correspondence to Jean Carter of your office last week, and a copy of the letter I had written Dean Born, Chief Inspector for the city of Slidell.

  The electrical Inspector for the city of Slidell is Dan Hooge.  His telephone number is 504-646-4323,

  The 1999 Electrical code, article 230-1, addresses the number of services allowed to one building.  230-(2b) addresses additional services and 2(b)-2 says “A single building or other structure sufficiently large to make two or more services necessary”, will be permitted to have more than one service. 

  Article 230 goes on to show allowances of multiple service for several different reasons such as 230 © (3) etc.

  Article 230-3 also states that one building or other structure not to be supplied through another.  In this case, the building is completely separated by a firewall that extends to the roof.  In effect, we then would not only have conductors passing through a firewall, but through an area that is in effect a building into itself.

  If permission is granted for this two services, 230-2 (e) will require that identification in the way of plaques be used to identify the existence of another services. 

  I appreciate your looking into this matter.  As you well know, we install separate services in shopping centers etc, on a regular basis.

Sincerely,

Emmett G (Pete) Dammon P.E.,

Attachments

     1.
 Letter from Steve Hill to Jean Carter 6/28/00

2. Letter from Steve Hill to Cynthia Oliver 6/22/00 

3. Letter from Pete Dammon to Dean Born  6/20/00

EGD/plc

