February 21, 2000

Plan Review

Office of the Fire Marshall

5150 Florida Ave

Baton Rouge, LA  70806

RE;
Woodson School Renovations, Smoke detection 


And Alarm section

Dear Sir,

  Please refer to the attached photos showing the beams that support the roof deck and/or second floor, in the hallways.  When  installing smoke detectors, we have elected to install one on every other beam shown, as opposed to each beam.

  By installing the detector at the bottom of the beam it will quickly pick up any products of combustion that would come from the next bay.  Each bay is approximately 300 cu. Ft. of space above the bottom of the beam.







Sincerely,







Emmett G (Pete) Dammon P.E.,

Attachments


Photos 1 thru 4

cc: Ted Harris, OPSB

plc/EGD

