Fax 646-6117/phone 646-4323
May 5, 2005

Mr. Kirk Pichon

City of Slidell

P.. Box 828

Slidell, LA  70459

RE:
220 Florida Ave.

Dear Kirk,

The following is in response to your letter dated April 3, 2005:

BUILDING:

1) Design Criteria

A.  Sheet has been revised.
2) 1603.1.4 Wind load

A.  Noted on cover sheet and on sheet A-5.
3) 1603.1.5 Earthquake design data.

A. 1.  1
2.  .14/.095

3.  D
4.  Group I, Design Cat. = A

5.  Group I, Design Cat. = C

6.  Min. lateral force, min. design lateral force.

4) 1706.1 Scope.

A.  Contractor shall supply this information.
5)  1003.3.1.8 Locks and latches

A.  Contractor shall comply with this.
6)  Table 602 would require a one-hour rating on left and rear exterior walls (Interior fire exposure only) cover sheet indicates 0 rating.

A.  Revised to match rated walls.
7)  716.2 Fireblocking

A.  Noted on sheet A-2
8)  1405.13 Vinyl siding

A.  Noted on sheet A-2.  Vinyl siding shall meet the 130 mph wind load and shall be installed per the manufacturer’s requirements.  Siding to be Owens Corning “Classic Siding” or equal.
Product Test Data:


Heat Shrinkage……………………………………<3% at 160°F

Impact Resistance…………………………………Mean Failure Energy >60 in. lb.

Static Windload Test Pressure…………………….40 PSF

Design Windload………………………………….149 MPH

Surface Distortion…………………….…………...None at 120°F

Squareness………………………………………...<1/8” of Square

Length……………………………………………..Within -¼” of Specification

Warp/Camber……………………………………...<1/8”

Coefficient of Linear Expansion (in./in.°F)……….3.15 x 10-5
9)  1202.2 Attic spaces.

A.  Noted on sheet A-2.
10)  1208.2 Attic spaces

A.  Revised door size to 2/0 x 3/0
11)  Please specify size of lam beam.

A.  Noted on sheet A-1 (revised – now using a W12 x 22 beam)
12)  2308.10.5 Purlins.

A.  Adjustment were made on sheet A-2.
13)  Please list specific connectors to be used, include hold downs, straps, uplift connectors, etc.

A.  See sheet A-6 for details.
14)  All applicable provisions of chapter 11 shall be met.

A.  Contractor shall comply with this.
15)  How are the ends of rafters being supported at front of building (Section A sheet A2)

A.  With a 2 x 6 @ 16” o.c. across porch tied into load bearing wall and columns.
MECHANICAL

No Comments

PLUMBING

No plumbing per plans

ELECTRICAL

No Comments

If you have any questions, please feel free to call.

Sincerely,

Chuck Dammon

VP/Project Manager

