July 6, 2005
Mr. Kirk Pichon

Plan Examiner

The City of Slidell

2055 Second Street

Slidell, Louisiana  70458

RE:
1030 Old Spanish Trail
Dear Mr. Pichon,

Following are answers to your letter dated June 30, 2005, copy attached.

BUILDING

1) Please provide drawings from metal building manufacturer, the drawings should include the following information:

1603.1.4 Wind load.

A.  Contractor shall provide at time of submittal.
2) 1603.1.5 Earthquake design data.

A.  Following is the earthquake design analysis for this project.

1. Seismic Group 1

2. Table 16151.1

Site Classification D

3.
Fa = 1.6
Fv = 2.4

4.
SMS = FA (1.6) x S5 (.14) - .224


SM1 = Fv (2.4) x S1 (.06) - .144


SDS = .66 (SM5 - .224) - .147


SD1 = .66 (Sm1 - .144) - .095

From 1616.3 (1), Group 1, = Design Cat. A

From 1616.3 (2) Group 1, Design Cat. C

5. Design Cat. A & C shall follow article 1616.4.1 through 1616.4.4 for design of structure.
6. IBC Code Book
3) 1003.3.1.8 Locks and latches.

A.  Contractor shall comply.
4) Please provide wind load calculations for overhead doors and storefronts.

A. Contractor shall supply .
5) Combustibles shall be allowed only in areas described in section 603 in buildings of type II construction.  (Platforms above bathrooms).

A.  Contractor shall comply.

MECHANICAL

1) Outside air requirements for each individual space shall be based on the use and occupancy of the space.

A. O.K. 

2) 405.1 General.

A.  Contractor shall comply.  

3) An air balance report shall be provided prior to final inspection to verify compliance with Chapter 4.

A. Contractor shall comply. 

If you have any questions, or require any further information, please feel free to call.
Sincerely,

Emmett G. (Pete) Dammon, P.E.
