April 4, 2003

Mr. Bob Hughes

Camco Construction, Inc.

725 Dove Park Rd.

Covington, Louisiana  70433

RE:
Shopping Center for Gary Mutter


Hwy 190


Slidell, Louisiana

Dear Mr. Hughes,

Kirt Pichon with the City of Slidell called and informed us of a new restaurant going in at this site.  This changes the classification from Mercantile to Assembly.

We will need a three-hour firewall separating the areas of the building to be under 12,000 square feet each.  With this three-hour firewall, we will not have to sprinkle the building.  Also, with this firewall there can be no openings of four-feet or less on either side of the firewall (ex. doors, windows, etc.).  The wind load shall be 130mph.  Please notify your building supplier.

If you have any questions, or require any further information, please feel free to call.

Sincerely,

Emmett G. (Pete) Dammon, P.E.

