DAMMON ENGINEERING, INC.
dammonengineering.com
ARCHITECTS




ENGINEERS


CONSULTING

DESIGN

STUDIES

EXPERT WITNESS


1095 Florida Ave.



   P.O. Box 2830



     985-649-5832

Slidell, LA 70458



Slidell, LA  70459


            FAX 985-641-5950

October 27, 2009
Attn:
Mr. Greg Wiltz

Lafayette Consolidated Government

220 W. Willow Street, Building B

P.O. Box 4017-C

Lafayette, Louisiana  70502

RE:
101 Marble Creek Cove

Lafayette, La 70508
Dear Mr. Wiltz,

This letter is to confirm that we have inspected the bonding system for the pool at this site and found it to be in compliance with the National Electrical Code.
The rebar steel is tied on 10" x 10" centers with deck dowel sticking up out of the rebar cage approximately 2' - 4' outside the gunite shell.  Standard ground clamps are installed to these dowels in 4 - 5 places around the pool.  Bond wire is run in a continuous loop starting at the equipment, thru the back of the light niche, thru each ground clamp attached to the deck dowels and continuing the loop back to the equipment pad.
We hereby notify you that we will take responsibility for the bonding system on the pool at this location.
Sincerely,

Emmett G. (Pete) Dammon, P.E.

