Electrical Inspections

● Pad Inspection – prior to pouring concrete when constructing “poured-in-place” pad (for location

only)

● Site Inspection minimum dimension from the generator or generator housing (when provided) to:

1. Lot lines or property lines – 2 feet

2. Combustible exterior building walls (including wood framed - brick veneer) = 5 feet min.

3. Openings located in an exterior wall of a building = 5 feet min. Sec. 4.1.4 of NFPA 37

4. Location and orientation of equipment in relation to the existing electrical panel

5. Electrical wire installation and conduit

6. Electrical contractor’s load analysis identifying the electrical loads selected, to verify

generator and transfer switch is appropriately sized for the designated loads

CONTACT INFORMATION