Job: Reinforcement of Incinerator Stack

Scope of Work:

1. Vendor is to supply all labor, materials and equipment needed to complete reinforcement of the Boiler Room Incinerator stack.  Vendor is to install rolled steel plate 3/16” thick is to be installed around the top three sections of the stack.  On the first bottom section, vendor is to install small 10” section of rolled steel that is missing from previous repair job.  All seams of these plates are to be welded completely around, top and bottom to the stack flanges; all side seams are to be welded completely.  The stack circumference is approx. 91” round and each stack section is approx. 60”L.

2. Vendor is to install four sections of 3”x 3” x ¼” angle iron, each approx. 20’ long, evenly spaced every 90 degrees around the stack; the bottom ends of the angle iron should rest on the top of the incinerator and be welded to the top of the incinerator box.  The angle iron should be cut/slotted at each stack section flange so that the angle iron will slide in and meet the newly installed stack shell and is be spot welded here on each side of the angle iron for its entire length.  Each spot weld should be 2” in length, spaced 10” apart; the angle iron should be welded the same on both sides, with the welds on each side staggered.

3. The existing top ring holding the spark arrestor wire guard is to be repaired if needed and spot welded every 6” to the new top section shell of rolled steel. Vendor is to supply and install a new spark arrestor wire over top of stack of same gauge wire material. 

4. Vendor is to install 3/16th steel flat plate on entire top of the incinerator main box; approx.     70” x 88” x 3/16th.  All seams of this plate are to be welded completely around; not spot welded.

5. Measurements previously taken are for designing these specs only.  Vendor is responsible for making all new measurements to complete the project properly.

6. Vendor is start within 30 days after being awarded the job and must complete this job within 45 days of being awarded the job bid. 

7. On site visit is required.

